General

Detailed

| Start Date: | Start Time: | Completion Date: | Completion Time: |
| --- | --- | --- | --- |
| QWEST Order Number: | Supplier Order Number: | System Type: |
| Central Office Name: | Central Office CLLI: | BAN#: | BVAPP#: | Date: |
| Design Engineer: | Installation Company: | Installation Representative (Print Name): |
| QWEST Representative (Approver - Print Name): | Installation Representative Contact #: |
| Job Description: |
| Job Type | Switch | Switch Power |
| Summary of Installed Equipment: |

Detailed below are all the steps necessary to explain the work that is to be performed.   Steps will be numbered, and appear in the order in which they will occur, with the work operation responsibility indicated by checking the appropriate boxes.  Work will not begin until this form has been reviewed and signed by QWEST and Supplier representatives.   This form may be duplicated if additional space is required.   All information must comply with QWEST Technical Publication 77350.

Have you Considered?

| Equipment Added | Emergency equipment & procedures available | Required Telco support |
| --- | --- | --- |
| Equipment Removed | Fuse alarm operation | Emergency restoration plans |
| Equipment Compatibility | Location of spare fuses | Fuses and leads tagged |
| Affected Working Circuits | Records correction | Office records/drawings available |
| Restricted work hours | Hazardous materials handling and disposal | Supplier drawings available |
| Work area protection | Personnel experience | Documents referenced in the MOP on-site |
| Special tools/materials | Before and after tests |  |
| Tool insulation | Back out procedures |  |
| Safety consideration | Technical reference |  |

| RESPONSIBILITY |  | STEPS COMPLETED |
| --- | --- | --- |
| S | S | Q | S | DESCRIPTION OF WORK OPERATION |  | INITIALS |
| T E P # | U P L | WE S T | S P * | (NOTE: Do not delete the shaded areas or the last row of this table) | D T A & I T M E E | S U P L | Q W E S T |
|  |  |  |  | IN THE EVENT OF A SERVICE INTERRUPTION, THE LUCENT LEAD INSTALLER MUST: 1. ASSIST IN RESTORING SERVICE 2. CONTACT CUSTOMER TECHNICAL SUPPORT (CTS) PHONE#: 1-(866) 582-3688 Prompt 1 3. AS IMMEDIATE AS PRACTICAL, THE LEAD INSTALLER SHALL SPEAK WITH ONE OF THE FOLLOWING PERSONNEL: OPERATIONS SUPERVISOR: OPERATIONS AREA MANAGER: SERVICE RELIABILITY MANAGER—Gilbert J. Sanchez (office) 720-482-4871 (cell) 303-885-3872 QWEST PERSONNEL WHEN FOLLOWING THE “HOT CUT” PROCEDURE. 4. OPERATIONS SUPERVISOR AND INSTALLER WILL DISTRIBUTE THE COMPLETED RG47-0013, SERVICE INTERRUPTION/DEGRADATION FORM, IAW QWEST TP77350, Ch. 13.8. |  |  |  |
|  | x | x |  | CAUTION: Please observe ALL prerequisites, cautions, and/or notes listed in the procedures and installation manuals. Failure to do so could cause harm to your self and/or put service at risk and/or failure. If at any time you do not get the desired response or you do not understand what is occurring, STOP! Immediately contact Regional CTS. |  |  |  |
|  | X |  |  | WARNING: Failure to verify use of the latest procedure can and has caused total system outages. Software changes are not made backward compatible with the old procedure. The responsibility for switch outages belongs to Installation if they are not using the absolute latest version of the procedure. If you cannot verify if you have the latest version then you should stop now until it can be verified. Verification should be performed just prior to the start of the procedure – not performed in advance. Indicate date you performed issue verification for each handbook section on pg 5 of this MOP (Documentation section). |  |  |  |
|  |  | x |  | THROUGHOUT THIS MOP A QUALIFIED QWEST TECHNICIAN WILL TURN DOWN, POWER DOWN, POWER UP, AND RESTORE ALL AFFECTED EQUIPMENT. |  |  |  |
|  |  | x |  | ALL IN-SERVICE EQUIPMENT WILL BE REMOVED AND RESTORED BY QUALIFIED QWEST PERSONNEL |  |  |  |
|  | X | x |  | THROUGHOUT THIS MOP, A QUALIFIED LUCENT AND QWEST TECHNICIAN WILL MAKE APPROPRIATE CHANGES TO THE RCV AND THE ECD DATABASES USING THE GRCV'S AND/OR HANDBOOKS USED BY LUCENT TECHNOLOGIES. |  |  |  |
|  | X | X |  | MECHANIZED GRCV’s WILL NOT BE USED TO GROW EQUIPMENT IN EXISTING SM’s |  |  |  |
|  | X | X |  | ST2000 WILL NOT BE USED TO TEST PERIPHERAL EQUIPMENT ADDED TO EXISTING SM’s |  |  |  |
|  |  | x |  | PRIOR TO START AND END OF EACH SHIFT, VERIFY OFFICE ALARMS FOR ABNORMAL CONDITIONS AND FIX OR NOTE ANY PROBLEMS |  |  |  |
|  | x | x |  | ALL ADDITIONS AND TESTING OF EQUIPMENT WILL BE DONE BY LUCENT PERSONNEL AND MONITORED BY QWEST PERSONNEL |  |  |  |
| 1 |  | X |  | OBTAIN PNAR FOR THIS ORDER. RECORD PNAR # ON THIS MOP. |  |  |  |
| 2 | X | x |  | DEDICATE FX LINE TO THIS ORDER (keep this line open and available for use in case of service interruption) |  |  |  |
| 3 |  | x |  | CONTACT NOC/SCC PRIOR TO THE START AND END OF EACH SHIFT USING FX LINE (this verifies the line is working) |  |  |  |
| 4 |  | x |  | VERIFY SWITCH CONDITION PRIOR TO EACH SHIFT |  |  |  |
| 5 |  | x |  | VERIFY ROP IS OPERATIONAL |  |  |  |
| 6 |  | x |  | BACKUP TAPES MUST BE MADE PRIOR TO STARTING THIS PROCEDURE; VERIFY BACKUP TAPES HAVE BEEN MADE WITHIN THE LAST 5 DAYS |  |  |  |

* (SSP)  Safe Stop Point

The undersigned have approved the procedures that are described herein. No changes shall be made without the approval of the QWEST, Installation Supplier, and Supplier Review Representatives.

| Service Supplier Representative: | Title: | Phone: | Date: |
| --- | --- | --- | --- |

| Service Supplier Personnel Performing work: | Title: | Phone: | Date: |
| --- | --- | --- | --- |
| Qwest SPOC: Brian Lunseth | Title: SPOC for Lucent | Phone: 612-663-2077 | Date: |
| QWEST Representative: | Title: | Phone: | Date: |
| QWEST LNO Technician: | Title: | Phone: | Date: |

| Issue Date | Documentation to be used on Job | Date Verified: |
| --- | --- | --- |
| 04/03 | QWEST 77350 ISSUE M |  |
| Verify latest issue | IG001 (various sections) |  |
| Latest issues | Job Specs, TEO, and Drawings |  |
| Verify latest issue | IEH 0 (various sections) |  |
|  | SIG-C-WU-100 Handbook Sections: |  |
|  | HB SECT 0506 Growth Sequencing |  |

DETAILED METHOD OF PROCEDURE - CHECK LIST OF PERTINENT ITEMS

**The following checklist shall be reviewed, completed, and signed during the “job start walk-thru” by the Supplier In-charge/Lead Installer and the Local On-Site Work Force.

Place a check in the boxes as each of the following items are discussed and agreed upon:

1.	Identify the equipment to be installed, modified, or removed (Copy of TEO / Spec, etc.).

2.	Compatibility of the proposed equipment with existing equipment.

3.	Identify the working telecommunications equipment that may be affected.

Is a detailed MOP required for (Complete Step-by-Step procedures, Page 1)	DATE

Transition of working circuits per page 4, item 9	YES 	NO

Proximity to working equipment	YES 	NO

Modifications to a working system	YES 	NO

Additions to a working system	YES 	NO

4.	When working equipment will be removed from out of service.

Is a detailed MOP required for:  (Complete Step-by-Step procedures, Page 1)		DATE

Removal of working equipment/circuits per page 4, item 9	YES 	NO

5.	Proximity of power plants distributing systems and location of office power down procedures.

6.	Where spare fuses are located.

7.	List the steps requiring the presence of a QWEST representative

8.	Alarms to be disconnected and schedule of disconnect.			DATE

Establish a power/switch alarm transition plan	YES 	NO

Daily visual inspection of power/switch plant alarms	YES 	NO

Joint power/switch alarm integrity tests	YES 	NO

9.	Records and Drawings to be corrected.

10.	Protection of floors, walls, etc.

11.	Storage of tools and materials.

12.	Safety precautions.

13.	Service restoration procedure and responsibilities in the event of service impairment.

14.	Identify the locations of essential and government circuits such as 911/FAA ckts. Ensure that they are

properly identified and labeled.

15.	Normal work shift.  Time to be stipulated: Start of shift      	 	End of shift      					Maintenance Window Waiver: YES  NO 	 If yes, requires QWEST Technical Support Authorization.

15a.	A green ANCR will be issued by QWEST/Vendor representatives: 	YES  	NO

16.	Disposition of removed equipment.  Does equipment need to be RGM to QWEST? 	YES 	NO

17.	List of office and emergency contact numbers for Vendor and QWEST representatives.

(This list must be posted in the office as well as attached to the MOP)

18.	Actions to be taken in the event that unusual conditions have occurred.  If service affecting, call NROC and                                follow your Service Interruption process.

19.	Is a planned Outage Report required?  (QWEST representative responsibility)  Green ANCR

##### DETAILED METHOD OF PROCEDURE - CHECK LIST OF PERTINENT ITEMS CONT’D

20.	Approvals are required for additions or changes to an approved MOP.

21.	Verify FX line is working properly before start of maintenance work.

22.	Is there sufficient storage space available at the site?	YES 	NO

If YES, show location, if NO, indicate solution:

23.	Is there a dedicated unpacking room at this site?	YES 	NO

If YES, show location, if NO, indicate solution:

NOTE: Room should not contain re-circulating Air Return Vents.  If so, contact Customer

Customer Response:

24.	Verify ROP, MCC and TLWS are on and in working condition prior to start of installation activity.

25.	Notify QWEST NROC before start of shift.

26.	Verify that no alarm conditions are present before beginning work.

27.	Call NROC with End-of-Shift report.

28.	Is building ready for installation?  	 YES 	 NO

If no contact the C.O. Manager and/or Building Engineer (CP).

29. **	Work assessment walk-through

Completed by	Date

SUPPLEMENTAL CHECKLIST

The following checklist is to be reviewed before the start of each shift and the In-charge or Lead Installer shall date and initial as appropriate.

| # | ITEM | Date and Initial | Date and Initial | Date and Initial | Date and Initial | Date and Initial |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Walk through performed by installer prior to each tour. | Y N NA | Y N NA | Y N NA | Y N NA | Y N NA |
| 2 | General mop written/approved. | Y N NA | Y N NA | Y N NA | Y N NA | Y N NA |
| 3 | Detailed mop written/approved. | Y N NA | Y N NA | Y N NA | Y N NA | Y N NA |
| 4 | Emergency contact list available to all installers. | Y N NA | Y N NA | Y N NA | Y N NA | Y N NA |
| 5 | Alarms verified for all associated equipment. | Y N NA | Y N NA | Y N NA | Y N NA | Y N NA |
| 6 | Protective material kit on job. | Y N NA | Y N NA | Y N NA | Y N NA | Y N NA |
| 7 | Is work area insulated with proper material? | Y N NA | Y N NA | Y N NA | Y N NA | Y N NA |
| 8 | Sharp edges covered in work area. | Y N NA | Y N NA | Y N NA | Y N NA | Y N NA |
| 9 | Cable ends covered with tape or tubing. | Y N NA | Y N NA | Y N NA | Y N NA | Y N NA |
| 10 | Fuses properly identified and sized. | Y N NA | Y N NA | Y N NA | Y N NA | Y N NA |
| 11 | Have cables been traced. | Y N NA | Y N NA | Y N NA | Y N NA | Y N NA |
| 12 | Cables are metered and tagged. | Y N NA | Y N NA | Y N NA | Y N NA | Y N NA |
| 13 | Are temporary cables properly secured and supported. | Y N NA | Y N NA | Y N NA | Y N NA | Y N NA |
| 14 | Are tools properly insulated? | Y N NA | Y N NA | Y N NA | Y N NA | Y N NA |
| 15 | Are guards in place on tools? | Y N NA | Y N NA | Y N NA | Y N NA | Y N NA |
| 16 | Is personal protective equipment available & being used? | Y N NA | Y N NA | Y N NA | Y N NA | Y N NA |
| 17 | TP 77350 procedures being followed. | Y N NA | Y N NA | Y N NA | Y N NA | Y N NA |
| 18 | Are customer standards understood and being followed? | Y N NA | Y N NA | Y N NA | Y N NA | Y N NA |
| 19 | Approved battery spill kit on site. | Y N NA | Y N NA | Y N NA | Y N NA | Y N NA |

ASK YOURSELF QUESTIONS

| # | ITEM | Date and Initial | Date and Initial | Date and Initial | Date and Initial | Date and Initial |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Do I know why I am doing this work? | Y N NA | Y N NA | Y N NA | Y N NA | Y N NA |
| 2 | Have I identified and notified everybody (customers and internal groups) who will be directly affected by this work? | Y N NA | Y N NA | Y N NA | Y N NA | Y N NA |
| 3 | Can I prevent or control service interruptions? | Y N NA | Y N NA | Y N NA | Y N NA | Y N NA |
| 4 | Is this the right time to do this work? | Y N NA | Y N NA | Y N NA | Y N NA | Y N NA |
| 5 | Am I trained and qualified to do this work? | Y N NA | Y N NA | Y N NA | Y N NA | Y N NA |
| 6 | Are the work orders, MOPs and supporting documentation current and error free? | Y N NA | Y N NA | Y N NA | Y N NA | Y N NA |
| 7 | Do I have everything I need to quickly restore service if something goes wrong? | Y N NA | Y N NA | Y N NA | Y N NA | Y N NA |
| 8 | Have I walked through the procedures? | Y N NA | Y N NA | Y N NA | Y N NA | Y N NA |
| 9 | Am I using the right tools to perform this work? | Y N NA | Y N NA | Y N NA | Y N NA | Y N NA |

(  IF YOU ANSWERED “NO” TO ANY OF THE ABOVE -- CALL YOUR SUPERVISOR PRIOR TO JOB START

The original MOP will be signed locally by the QWEST C.O. Manager or designated personnel.

| Contact list for QWEST: | Contact list for Vendor: |
| --- | --- |
| C.O. Manager: |  | Installation Director: |  |
| Office Technician: |  | Installation OAM: |  |
| C.O. Director: |  | Installation Supervisor: |  |
| Tech Support: RTAC/CTS | 866-582-3688 Prompt 1 |  |  |
| Tech Support: ESAC | 303-707-5560 |  |  |
| Tech Support Mgr.: Kevin Kerkvliet | 612-663-2033 |  |  |
| Tech Support Director: Jim Steiner | 303-707-5608 |  |  |
| Project Manager: |  |  |  |
| Project Director: |  |  |  |