## How to
This is a workbook to help you prepopulate the required forms for Central Office
Installation jobs.
1. Completely fill out the page named "General Info". This can be done by clicking on the tab
marked General info at the bottom of the workbook. This information will be populated on each
form, where indicated in this workbook. If some of the fields are not applicable, leave them blank.
2. Do not leave the info that is in there from a previous job.
3. Each form can be accessed by clicking on the appropriate tab at the bottom of the screen if
needed.
4. Preparing to email your workbook.
To delete forms that are not applicable to your job, click on the tab that contains the form.
Click on "Edit" on the top toolbar, click on "Delete Sheet". Once you have completed the workbook
and all of the appropriate forms are contained in the file, click on "Save as" and enter the BVAPP#
in the file name. Make sure the file is saving to the the shared folders as specified in the process so you
or your co-workers can easily retrieve the workbook and will know where it is contained.
DO NOT DELETE THE GENERAL INFO PAGE. THIS PAGE CONTAINS ALL OF THE DATA
AND LINKS FOR THE PRE-POPULATION OF THE FORMS WORKBOOK.
5. Printing (only if needed).
To print the entire pre-filled workbook, click on the "AA Coversheet" tab. Then click on the shift key
and click on the last tab of the workbook.
For collo jobs, the CLEC forms will need to be printed.
You can print multiple forms by clicking on the first tab you wish to print, the click on
the Control key and click on the tabs of any other form you wish to print.
For Power jobs, the Power forms may need to be printed.
You can print multiple forms by clicking on the first tab you wish to print, the click on
the Control key and click on the tabs of any other form you wish to print.
Once you have determined what forms you wish to print, click on File and then print or click
the little printer ICON on the top of the page.

## General info
Fields in RED must be by the WMC AA. Fields in Blue are Required for CLEC jobs and filled by the WMC AA. Fields in Black are filled out by the installer
BVAPP
Job ID
CLEC Name
CLEC location ID
CLLI
Address ID
Central office name
CO Address
City,State, Zip Code
Design Engineer
Design Engineer RC code
Installation Company
Installation manager
Managers phone number
Analytical Associate
AA Phone
AA Fax
WFA Ticket Number
Installers name
Installers pager number
Authorized phone number
Authorized fax number
Staging location
Admin Location
CO Manager
CO Phone number
Scheduled start date
Actual start date
Scheduled completion date
Actual completion date
PNAR
Job description
Summary of equipment involved
NMA number
Marked drawings
Nature Of Work/Desc:
Note on B2: Qwest: Please use capital letters.
Note on B6: Qwest: Please use capital letters
Note on B4: Qwest: Use only for collo jobs
Note on B3: Qwest: This is the same as the BAN #. Please use capital letters
Note on B5: Qwest: Please use capital letters
Note on B22: Qwest: Telephone number CO ops will let you use during installation
Note on B23: Qwest: Fax numberCO ops will let you use, usually the CO fax number in that office.
Note on B24: Qwest: Location in CO where equipment to be installed is stored.
Note on B25: Qwest: Locaton where in CO where you perform paper work
Note on B33: Qwest: List the equipment added
Note on B34: Qwest: List the equipment added
Note on B36: Qwest: Insert Yes or No and if Yes, date sent to engineer.

## AA Coversheet
0
THIS JOB PACKAGE WAS PREPARED BY:
PREPARED BY:
0
PHONE:
0
FAX:
0
IN THE EVENT OF AN OUTAGE OR EMERGENCY CALL:
AZ,CO, ID, MT, NM, UT, & WY – 800-830-0722
IA, MN, ND, SD, NE, OR & WA – 800-341-8188
TO OBTAIN A PNAR (PLANNED NETWORK ACTIVITY NUMBER)
PLEASE CALL 1-800-258-8144.
NMA Group Phone: 800-557-0778, Option 1 Fax: 612-663-3015
http://saw3.uswc.uswest.com/NROC/NMAD/Nnmadbply.html
UPON COMPLETION OF THE JOB
PLEASE RETURN TO:
Work Management Center (WMC)
ATTENTION:
0
700 W. Mineral, Wyoming
Littleton, Co. 80120

## NAVL WAREHOUSES
0
PHOENIX,AZ | NAVPHAZ | TUCSON, AZ | NAVTUAZ
AMERICAN WESTERN DISTRIBUTION |  | RALPH TRANSFER
1511 S 47TH AVE. |  | 4051 S LONGFELLOW AVE
85403 |  | 85714
KAREN BELLAR (602)-272-6016 X205 |  | MARC ESPINOZA 520-622-6461
JOE VALENZUELA (602)-272-6016 |  | MEREDITH LOCKETT 520-622-6461
DENVER, CO. | NAVDECO | COLORADO SPRINGS, CO | NAVCOCO
CDG COLORADO DISTRIBUTION GROUP |  | ARROW MOVING & STORAGE
4725 LEYDEN, SUITE D 80216 |  | 2885 JANITELL ROAD EAST
1ST CONTACT DIRECT LINE 720-377-0523 |  | 80906
2ND CONTACT CRYSTAL ELKERTON 303-847-7232 |  | PAUL GREER (719)-527-0616
3RD CONTACT WENDI PORTMAN 512-731-6750 |  | SHELDON PERINO (719)-527-4822
GRAND JUNCTION, CO | NAVGRCO | CHEYENNE, WY | NAVCHWY
MESA MOVING AND STORAGE |  | BURKE MOVING AND STORAGE
681 RAIL ROAD BLVD |  | 388 NORTH AMERICAN ROAD
81505 |  | 82007
MARC THOMPSON (970)-242-1565 EXT.349 |  | BARRY RYERSE (307)-632-5536
TERRY KING (970)-242-1565 EXT 369 |  | BRYAN SCADDEN (307)-632-5536
CASPER, WY | NAVCAWY | BOISE, ID | NAVBOID
WYOMING TRANSFER |  | AIR VAN NORTH AMERICAN
330 SOUTH SPRUCE ST. |  | 12368 WEST MONSANTO STREET
82601 |  | 83713
CAROL (800)-711-3826 |  | DAWN URATA (208)-341-1088
JIM SEE (307)-259-0840 CELL, HM (307)-265-0956 |  | DAVE BOWMAN (208)-341-1081
POCATELLO, ID | NAVPOID | JOHNSTON, IA | NAVDEIA
LEE HAWKES TRANSFER |  | BELTMANN NORTH AMERICAN
848 SOUTH 1ST STREET |  | 5605 NORTHWEST 100TH ST.
83201 |  | 50131
KATHY ADAMS (800)-777-4395 |  | KELLY LEUTZINGER (515)-986-5559
BRYAN COOPER (208)-233-2337 |  | GREGG. (800)-398-5550
NORTH LIBERTY, IOWA | NAVIOIA | ST PAUL, MN | MANSTMN
HAWKEYE NORTH AMERICAN |  | BELTMANN NORTH AMERICAN
2870 STONER COURT |  | 2480 LONG LAKE ROAD
52317 |  | ROSEVILLE, MN 55113
JULIE KRETZSCHMAR (800)-397-3700 EXT. 230 |  | JOHN ROIGER (800)-949-8880 EXT. 2880
MICHELLE HUFF (319)-665-4020 EXT. 224 |  | GLENN WEAKLEY (651)-639-2910
BILLINGS,MT | NAVBIMT | MISSOULA, MT | NAVMIMT
KING TRANSFER |  | MONTANA TRANSFER COMPANY
7232 GRAND AVE. |  | 200 TRADE STREET
59106 |  | 59808
Gerrick Angel (406)-656-5464 |  | JARRET HOKE (800)-447-7557
ALLAN NICHOLS (406)-252-6394 |  | CLINT BAERTSCH (406)-728-8080
FARGO,ND | NAVFAND | BISMARK,ND | NAVBIND
FETTES MOVING AND STORAGE |  | JOBBERS MOVING & STORAGE
3939 7TH AVE |  | 1200 INDUSTRIAL DRIVE
58102 |  | 58501
ARLENE DITTUS (800)-325-3696 |  | JANICA SOBOT (701)-222-1111
DAVE GLASER (701)-277-3631 |  | CINDY TERNS (701)-222-1111
OMAHA, NE | NAVOMNE | ALBUQUERQUE, NM | NAVALNM
ACE STORAGE |  | ALBUQUERQUE MOVING & STORAGE CO
7820 L STREET |  | 5001 PASEO DEL NORTE NE
68127 |  | 87113
SCOTT VAUGHN (402)-593-1234 |  | LES SMITH 505-823-1441
KATHY WALKER (402)-593-1234 |  | JOE BACCA 505-823-1441
Page 1 of 2
0
EUGENE, OR | NAVEUOR | PORTLAND,OR | NAVPOOR
LILE NORTH AMERICAN |  | AIR VAN NORTH AMERICAN
3330 ROOSEVELT BLVD. |  | 119999 S.W. 95TH PLACE
97402 |  | TUALATIN 97062
SUE STRIBLING (541)-689-6683 |  | STEPHANIE BOETGER (800)-862-4801
BOB HIXSON (541)-683-3900 |  | AUTUMN MENDENHALL (503)-885-2353
PASCO, WA | NAVPAWA | MEDFORD, OR | NAVMEOR
AIR VAN NORTH AMERICAN |  | CUMMING TRANSFER
2440 E. AINSWORTH |  | 2061 LARS WAY
99301 |  | 97501
RANDY COX (800)-456-0925 |  | NITA LAMB (800)-866-9640
ERIC BENDER (509)-547-0528 |  | ED WELCH (541)-772-6278
SPOKANE, WA | NAVSPWA | SEATTLE, WA | NAVSEWA
LILE MOVING AND STORAGE |  | AIR VAN NORTH AMERICAN
E 7017 MISSION |  | 1500 INDUSTRY ST, STE 300
99212 |  | EVERETT 98203
TIM ORSBORN (800)-543-1554 |  | SANDY ARMBRUSTER 425-350-2177
DIANA DAUTER (509)-534-1554 |  | sarmbruster@airvan.net
RAPID CITY, SD | NAVRASD | SIOUX FALLS, SD | NAVSISD
GREENS MOVING & STORAGE |  | BROUWER RELOCATION
1115 EAST NEW YORK STREET |  | 3503 N. 1ST AVE
57701 |  | 57104
GAY WHALIN (605)-342-7060 |  | JARRED BROUWER (605)-333-0620
BRADY CHRISTOFFERSON |  | BRANDI MEYER (605)-333-0620
SALT LAKE CITY, UT | NAVSAUT
REDMAN VAN AND STORAGE
2589 S.2570 W.
WEST VALLEY CITY 84119
LYNN CHANDLER (800)-733-6261
DEBBIE SMITH (800)-733-6261
IF CONTACT CAN NOT BE MADE WITH NUMBERS
PROVIDED ABOVE, PLEASE CONTACT:
JEFF RYAN 303-599-1902 PAGER
OR JOHN RULLA 303-707-3111
Page 2 of 2

## Excess Warehouses
0
EXCESS MATERIAL WAREHOUSES
ARIZONA
VALLEY NORTH AMERICAN
1511 S 47TH AVE.
PHOENIX, AZ. 85403
Contact: KAREN BELLAR
Phone: 602-272-6016 X205
Fax: 623-936-2683
COLORADO
A-1 Relocation
11701 E 33RD AVE.,
AURORA, CO. 80010
Contact: DANIEL HERNANDEZ
Phone: 303-364-2684 EXT. 5519
Fax: 303-364-0903
OREGON
Air Van North American
20141 SW 95th Place
Tualatin, OR 97062
Contact: ROBERT ADAMS
Phone: 503-380-0657
Fax: 503-885-2363

## Job Start Policy
0
Job Start Policy
1) Installation crews will complete the following “Job Start” functions no later than 3 calendar days after
the DWP Materials Availability date. This is to occur even if there is insufficient material to actually start
the physical work on the job in order to identify and solve all potential installation problems early in the process.
2) Completing the “Job Start” function is defined as:
a) Verifying the installer has the latest DWP (check IOT or DWP server).
b) Identifying whether the job is feasible, as engineered, to include:
i) Determining that all cable-racking runs required to complete the job are not impeded.
ii) Determining that all cabling radius bends can be installed to 77350 standards.
iii) Determining that all assignments for power, signal, synch, etc. terminations are available.
iv) Determining that the materials ordered on the job spec allows the satisfactory completion of the job.
c) Identifying materials issues:
i) All materials ordered have been received by the installation crew, or have been verified to be available
at an off-site storage facility.
ii) This verification is not merely a check of a Procurement system. It is a physical check of as many of the
package contents as practical to ensure that the materials meet the job requirements and Job Finder
Report contents. The purpose is to identify engineering ordering or materials delivery problems as
early as possible.
iii) Examples (not meant to be all-inclusive):
(1) Actually open boxes to check packing slips vs. contents.
(2) Do not need to unravel cable reels to verify footage, but be aware as installation progresses.
(3) Check that BOM and packing slip and item itself are consistent.
(4) Check to see that panels that expand bay capacity are the correct type.
iv) Ensuring that any additional material needs are identified and ordered as soon as possible.
d) Identifying Real Estate items - (e.g Cable holes cut, Unistrut satisfactory, Collocation Cage placed, etc.)
e) Filling out and obtaining CO Operations’ signature on the General Method of Procedure. The MOP may be
posted in the Central Office, in the possession of the CO Ops Rep, or in the possession of the installer for
unstaffed locations.
f) When on-site construction actually commences and work on live network equipment is anticipated:
i) Ensure that a PNAR is opened using http://lno.uswc.uswest.com/cgi-bin/pnar/PNAR.pl
or by calling the appropriate center.
ii) Log the PNAR # in IOT.
3) Beginning the physical work on the job is required within 3 business days of posting the General Method
of Procedure (MOP) unless supported by a Date Management Root Cause code entered in IOT as a Job Start
note which explains the delay (see codes listed below).
4) COMMUNICATIONS - When the "Job Start" functions are complete:
a) IOT will be updated by filling out the IOT Electronic MOP with the following information
i) For Customer Premise jobs note who signed MOP (can be appropriate QTI Sup, Field Eng., DS Rep,
or CO Rep).
ii) For all other C.O. jobs:
(1) Note who signed the MOP.
(2) Note that the MOP is either posted or provided to CO Ops.
b) Notes of any issues uncovered during the above checks will be entered as needed and documented on
proper job forms (including who was contacted to resolve).
Root Cause Codes
1. AMC (Incorrect configuration)
2. Site Survey (Site survey incomplete or not done)
3. Planning (Standard intervals, CPD incorrect)
4. Detail Engineering (Design issue, incorrect material ordered, drawings not updated or
incomplete, received unreasonable or incorrect dates)
5. Material (Damaged material, backorder, incorrect PID)
6. Installation (Resource issue, re-work issue)
7. Customer (Customer not ready)
8. Scheduling (Reschedule due to higher priority job, removed from hold)
9. Power (No power available)
10. Real Estate (Building not ready)
11. Central Office Operations
12. WMC (Info late to field, job not assigned)
13. Quality (Pre-existing condition to fix, re-work due to request from quality) Note: Examples not all inclusive.
14. Weather
15. At DWP release negotiated date.
16. Right of Way issues (radio jobs)

## Document Routing Checklist
0
DOCUMENTS TO OTHER DEPARTMENTS (QTI, WMC, Engineering, etc.) | In IOT | White Envelope | Sent in Elec Workbook
MOP/General & Detailed RG47-0005 & RG47-0162 (Posted MOP should be placed in white envelope) | X | X | N/A
Job Log RG41-0046 | X | N/A | N/A
Material Shortage Form RG47-0166 (may need to fax or email copy to WMC during job) | N/A | N/A | X
Central Office Common Systems Order Form RG47-0165 (may need to fax or email copy to WMC during job) | N/A | N/A | X
Test Record(s) RG47-0157 | N/A | N/A | X
Job Information Memorandums (JIMS) RG47-0004 | X | N/A | N/A
Letter(s) Of Deviation (if issued) RG47-0169 (email electronic copy or fax to WMC along w/elec workbook) | N/A | N/A | X
Service Interruption / Degradation Report (if problem occurred) RG47-0013 | N/A | N/A | X
Installation Assignment & Capacity Sheet (Alarm sheet) RG41-0170 (still need to fax or email a copy to Alarm Center & Engineer) | N/A | N/A | X
Installation Revised / Completion Form RG47-0002 (If walkthrough occurs, place initialed copy in white envelope. If walkthrough doesn't occur, no need to put paper copy in white envelope) | X | X | N/A
Document & Material Disposition RG33-0043 (Installation may insert a copy in the white envelope but it is not required) | N/A | N/A | X
Quality Checklist RG47-0161 | N/A | N/A | X
Certified Local Exchange Carrier (CLEC) Report RG47-0160 (must also leave copy in CLEC cage or posted at CLEC site) | N/A | N/A | X
Request for Disposition of Qwest Communications Material RG47-0010 (Email or fax copy to WMC so engineer can determine disposition) | N/A | N/A | X
Bill(s) of Lading RG33-0017 (Keep copy in white envelope) | N/A | X | N/A
Marked Drawings (leave one copy in White envelope, send 2nd copy to WMC if applicable) | N/A | X | N/A
Report of Equipment Disconnected from Plant RG47-0009 (Removal jobs only) | N/A | N/A | X

## RG33-0043 Material Disp
Document and Material Disposition
City, State |  |  | Office |  |  | BVAPP |  | Job ID | Date
0 |  |  | 0 |  |  | 0 |  | 0
Job Type
IOF |  | XDSL/Megabit |  |  |  | Power |  | Collocation | Other
Line | Item No. | Quantity |  | √ | Description |  |  |  | Part No.
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
Remarks:
Form Completed by: | [6 empty] | Material/Document Received by:

## RG47-0001 Storage Battery Repor
STORAGE BATTERY CHARGE RECORD AND END OF CHARGE REPORT
(Note: Use one set of forms per string and Ref. 77350, Chapter 10)
Page 1 of 2
JOB INFORMATION |  |  |  | BATTERIES AS RECEIVED OPEN CELL DATA | [7 empty] | BATTERIES AT TURNOVER (ON FLOAT)
(Note: Must be on float at least 24 hrs.)
|  |  |  | Cell # | SERIAL # |  | MFG. Date | Voltage | Specific Gravity | Acid Level |  | Cell# | Voltage | Temp Deg. F. | Specific Gravity | Voltage within 2.17V 2.27V
Plant ID:
String ID: | [15 empty] | (Y or N)
CENTRAL OFFICE |  | 0 |  | 1 | [7 empty] | 1
ADDRESS |  |  |  | 2 | [7 empty] | 2
0 |  |  |  | 3 | [7 empty] | 3
CITY & STATE |  |  |  | 4 | [7 empty] | 4
0 |  |  |  | 5 | [7 empty] | 5
SUPPLIER |  | 0 |  | 6 | [7 empty] | 6
SUPP. ORDER# |  |  |  | 7 | [7 empty] | 7
BVAPP # |  | 0 |  | 8 | [7 empty] | 8
JOB ID # |  | 0 |  | 9 | [7 empty] | 9
ADDRID |  | 0 |  | 10 | [7 empty] | 10
CLLI CODE |  | 0 |  | 11 | [7 empty] | 11
INSTALLER NAME |  | 0 |  | 12 | [7 empty] | 12
BATTERY MFG |  |  |  | 13 | [7 empty] | 13
BATTERY MODEL |  |  |  | 14 | [7 empty] | 14
CATALOG# |  |  |  | 15 | [7 empty] | 15
DATE RECEIVED |  |  |  | 16 | [7 empty] | 16
CHARGE BY DATE |  |  |  | 17 | [7 empty] | 17
TORQUE Value |  |  |  | 18 | [7 empty] | 18
PLANT Float Voltage |  |  |  | 19 | [7 empty] | 19
NOMINAL Float Voltage |  |  |  | 20 | [7 empty] | 20
TEMP.REF.CELL # |  |  |  | 21 | [7 empty] | 21
TURNOVER DATE |  |  |  | 22 | [7 empty] | 22
Turnover Avg. Voltage |  |  |  | 23 | [7 empty] | 23
ACCEPTED BY: |  |  |  | 24 | [7 empty] | 24
FOOTNOTES
| 1. Nominal float voltage is plant float voltage divided by the number of cells in the battery string | [8 empty] | 5. Batteries must be on float 24 hours. Before connecting to plant.
| 2. At turnover each cell must measure between -2.14V and -2.27V | [8 empty] | 6. Acid Level: check to see if the acid level is acceptable; if so mark O.K.
| 3. Accepted By: must be a Power Tech. Or COT/Supv. In charge | [8 empty] | 7. All measurements shall be rounded to the nearest 100ths digit
| 4. Temp.Ref.Cell will be selected as Defined in 77350, chapter 10 | [8 empty] | (Ex: 2.511V through 2.514V = 2.51V, and 2.515V through 2.519V - 2.52V)
STORAGE BATTERY CHARGE RECORD AND END OF CHARGE REPORT
(Note: Use one set of forms per string and Ref. 77350, Chapter 10)
Page 2 of 2 |  | 0
Plant ID:
String:
| {Cell Voltage readings for first 100 hrs. of charge} | [5 empty] | {Additional Hours of Charge as Needed}. |  |  |  |  | {End of Charge Readings}.
DAY | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | Volts | Specific Gravity | Temp
DATE
TIME
CELL#
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
Charger AMPS
Charger voltage
FOOTNOTES
1. Battery charger must be able to supply enough current and voltage to bring the string up to charge level. The charger shall be
at least 1/100th of the battery amp hr. rating. Example 4000 amp hr. batteries would require a min. 40 amp charger.
2. Charge level is when the (First) cell reaches 2.38V to 2.50V, per mfg. Requirements (Do not exceed 2.55 V on any of the cells
during this charge process). When this level is reached the 100 hours (minimum) of charge is started to bring all the cells up to this level.
3. End of charge readings are taken when:: Three consecutive hourly readings show each cell remains at its previous hourly reading,
while still on charge. Average charge level is ; the total of all cell readings divided by the number of cells in the batttery string.

## RG41-0046 Job Log
INSTALLATION JOB LOG RG41-0046
BVAPP #
0
DATE: | DETAILS:

## RG41-0170 Alarm Assgn, pg 1
| 0 | [5 empty] | Page 1 of 2
INSTALLATION ALARM ASSIGNMENT AND CAPACITY SHEET #1
|  | Date Faxed: |  | Number of pages including cover sheet:
1. | To: NMA DATABASE |  |  | 2. | From: INSTALLER
| Name: |  |  |  | Name: | 0
| Phone #: 800-557-0778 Opt 1 |  |  |  | Phone #:
| Fax #: 612-663-3015 |  |  |  | Page #: | 0
[5 empty] | Vendor Name: | 0
To: QWEST ENGINEER
CLLI: ____________________________ BVAPP #: ____________________________ EST #: ____________________________
| Name: | 0 |  |  | CLLI: | 0
| Phone# |  |  |  | BVAPP #: | 0
| Fax# |  |  |  | EST #: | 0
3. | IS THIS JOB AN ALARM ADDITION: |  |  | OR | REMOVAL:
4. |  |  | INSTRUCTIONS FOR COMPLETION
All jobs requiring alarms must be surveyed at Job Installation Start. The installer WILL be responsible for completing the Installation Assignment and Capacity Sheet and faxing (Cover page and all Assignment page(s)) to both the Qwest Engineer and the NMA Database Group, within a minimum of 48 hours up to a maximum of 72 hours of installation complete.
Before the job is completed the installer WILL be responsible for wiring and testing all Discrete and Serial alarms required with the NMA Database Group (Phone #763-536-3888). After testing, NMA will issue a LOG #. Record LOG # on Installation Alarm Assignment & Capacity Sheet and on the RG-47-0002 (ICN - Installation Completion Notice). If there were alarms that could not be tested the Installer WILL fill out the Alarm / OSS Testing Incompletion Tag, including the NMA LOG #, and tie it onto the appropriate piece(s) of equipment. In the Capacity Note Section, located on Sheet 2, provide any information concerning capacity needs and / or requirements for future installations.
EXPLANATION OF FIELDS
| 1. | NMA Database Group and Qwest Engineer contact information to be supplied by Installer.
| 2. | Installer information (including job information) to be filled out by Installer completing the form.
| 3. | Designate whether this job adds alarms or removes alarms, NMA needs all information either way.
| 4. | Instructions for filling out the Installation Alarm Assignment and Capacity Sheets 1 and 2.
| 5. | Installer name, phone # (and/or page #), etc., to be filled in by the Installer before faxing.
| 6. | After testing record LOG #, issued by NMA.
| 7. | Capacity Notes are to be used to identify potential shortages in Discrete & Serial alarms, for
future growth.
| 8. | Alarm Bay is the Relay Rack location of the bay containing the alarm equipment.
| 9. | Shelf is the shelf designation for the alarm assignments.
| 10. | ETEL is the designation for the alarm assignments.
| 11. | Address/Remote (alarm).
| 12. | Additional Comments
| 13. | If alarms can not be tested; Fill out Alarm / OSS Testing Incompletion Tag; Attach (w/string) to
each piece of equipment (i.e. shelf). This may require more than (1) one Alarm / OSS Tag.
Note on F3: Qwest: put date in this cell
Note on D6: Qwest: Name of person you are faxing form to.

## RG41-0170 Alarm Sheet, pg 2
Page 2 of 2
5. | Installer: | 0 |  |  |  | Phone #: |  |  | Pager #: | 0 |  | PIN# |  |  | Vendor |  | 0
| CLLI: | 0 |  |  |  | BVAPP: | 0 |  | JOB ID#: | 0
6. | LOG #: | [5 empty] | NMA Phone #: 800-557-0778 Opt 1 / NMA Fax #: 612-663-3015
7. | Discrete & Serial CAPACITY NOTES:
SERIAL ALARMS:
8. | Alarm Bay: RR |  |  |  |  | 8. Shelf: |  | 9. ETEL: |  |  | 10. Address/Remote(#)
ALARM UNIT INFORMATION
| MAP | MAC | PORT | DISPLAY# | SDR # | EQUIPMENT TYPE / RR / SHELF |  |  |  |  | TERMINAL |  | PUNCHING |  |  | LEAD XMT+ XMT- RCV+ RCV-
| Serial Alarms Tested By: | [7 empty] | Date:
DISCRETE ALARMS:
8. | Alarm Bay: RR |  |  |  |  | 8. Shelf: |  | 1.54 |  |  | 10. Address/Remote(#) |  |  | 31
|  |  | DATA BASE INFO |  | TERMINATING EQUIPMENT (NE) INFORMATION | [7 empty] | EQUIP X-CONN |  |  | ASSN X-CON
| SDR # | *BIT | Alarm Message |  | Equipment Type / RR / Shelf |  |  | Intfc Dwg | Figure | TS | Alm | Rtn | TB | Alm | Rtn | TB | Alm | Rtn
* Place a BIT/C in the BIT column if alarm is wired-out Normally Closed
| Discrete Alarms Tested By: | [7 empty] | Date:
12. | Additional Comments: |  |  | We will call tomorrow to figure out how we want to test working Eqpt.
13 | If alarms can not be tested; Fill out Alarm / OSS Testing Incompletion Tag; Attach (w/string) to each piece of equipment (I.e. shelf). This may require more than (1) one Alarm / OSS Tag.
NOTE: If more space is needed to record alarms use additional copies of this sheet / or attach blue line with all the appropriate information.
Note on C8: Qwest: This number need to be entered in the log also.

## JIM-ICN Categories Sheet
0
Categories Sheet
Job Extension Notice Categories (used as a part of the Date Management Process)
1. AMC (Incorrect configuration)
2. Site Survey (Site survey incomplete or not done)
3. Planning (Standard intervals, CPD incorrect)
4. Detail Engineering (Design issue, incorrect material ordered, drawings not updated or incomplete,
received unreasonable or incorrect dates)
5. Material (Damaged material, backorder, incorrect PID)
5a. Material (Damaged/Defective)
5b. Material (Incorrect Material Ordered)
5c. Material (Lost/Stolen)
5d. Material (Materials haven't shipped/arrived)
5e. Material (Materail not ordered
5f. Material (Incorrect materials shipped)
6. Installation (Resource issue, re-work issue)
7. Customer (Customer not ready)
8. Scheduling (Reschedule due to higher priority job, removed from hold)
9. Power (No power available)
10. Real Estate (Building not ready)
11. Central Office Operations
12. WMC (Info late to field, job not assigned)
13. Quality (Pre-existing condition to fix, re-work due to request from quality) Note: Examples not all inclusive.
14. Weather
15. At DWP release negotiated date
16. Right of Way issues (radio jobs)
17. Testing (NMA or sync testing needed for job to be complete)
JIM Form Categories
A. This type of JIM would be entered by QTI as a means of providing critical information to the engineer without an amendment or a change required in the IOT raking. Create a JIM but do not create an amendment.
B. This type of JIM would be entered by QTI if the job is in jeopardy of going over the IOT raked hours. Create a JIM & amendment - input # of hours in Qty field of the amendment using the "Misc" code. Use as much detail as possible for tracking purposes.
3. Electrical Contractor JIM – WMC AA creates a JIM but does not create an amendment unless Electrical Work was performed by QTI. If QTI performs the work, they will enter a JIM and create an amendment using the number of hours in the Qty field of the amendment and using the "Misc" code.
MD. Marked Drawings JIMs are entered by the WMC AA as a means of tracking the updates as submitted by QTI and entered in to COEFM by the engineer.
RG. RG47 JIMs are entered by the WMC AA as a means of tracking the progress of the RG47-0010 disposition of material form.
JIM Common Issues
Consumable Material - We do not pay for extra installation time for installing any consumable material.
Collocation Decommission Jobs - JIMs/Quotes must always be submitted to get the time necessary in IOT. Use JIM Category B, MISC Labor code. These JIMs should be submitted prior to the work beginning, if possible. If the Engineer has allocated X dollars in CPD, the AA would not be required to distribute the JIM.
Switch Quotes - JIMs/Quotes must be submitted by the WMC AA to get the time necessary in IOT when raking does not occur. Use JIM Category B and the appropriate Labor codes in the IOT amendment. These JIMs should be submitted prior to the work beginning.
AC Electrical Work - IOT does not rake for this work. If the work is done by Installation, create a JIM using Category 3 using the MISC labor code to recover the hours in IOT.
Items contained on BOM but not raked correctly - If an item is contained on the BOM but does not get raked by IOT, contact the WMC data team to ensure the part # is loaded into the catalog. When the job completes and the item has still not raked, insert a JIM using Category B and the appropriate Labor code.
Power Jobs - If appropriate raking does not occur, then QTI will use JIM Category B to document time in IOT. All JIMs for Power jobs will be distributed to the engineer.

## RG47-0002 ICN
Installation / Revised Completion Notice
Confirmation of Installation Completion
|  |  |  | Network Monitoring and Analysis (NMA) Confirmation # |  |  |  |  | 0 |  |  |  | Partial
Final
[6 empty] | PNAR # |  |  | 0
| Request for Revised Completion | [11 empty] | Extension
PNAR Closed Date
Marked Drawing, Date sent to WMC
Job-related materials & documentation handed over to CO Operations w/ signed RG33-0043.
Changed "Continuous Ship" address to immediate supervisor for materials borrowed from another job.
City, State, and Zip |  |  |  |  | Office / CLLI |  |  |  |  | Design Engineer's Name
0 |  |  |  |  | 0 |  |  | 0 |  | 0
BVAPP # |  | 0 |  |  | Job # | 0 |  |  |  | WFA # |  | 0
Scheduled Dates: | [5 empty] | Start | 0 |  |  | Complete |  | 0
Actual or Extension date: | [5 empty] | Start | 0 |  |  | Complete |  | 0
STRUCTURE | [14 empty] | Y/N/NA
Are the Frame/Bay/Cabinet top supports attached and secure?
Is the Frame/Bay/Cabinet grounded?
Are the Floor/Wall penetrations designated and fire stopped? (List holes used) Fire block Label (RG47-0133)?
Is the Illumination adequate?
Are the AC conduits and outlets located per specification (Typically front & rear of every 3rd bay)?
Are the combustibles and excess material cleaned up?
EQUIPMENT |  |  |  |  | LOCATION (RR, Shelf, block, jack, etc.) |  |  |  |  | Tested Y/N/NA |  |  | Designated Y/N/NA
Bay / Equipment Added
BDFB / PBD / Fuse Panel
DS0 MDF Vertical / Horizontal
DSX-1
DSX-3
Fiber Cables
Synchronization Cables
Alarm Cables
COLAN cables
Other
Job Package (All references in TP 77350 Issue M, Chapter 13.4)
Design Work Package (DWP) |  |  |  |  | Release # |  |  |  |  | Date:
Circuits and cables tested?
Has equipment that has been removed been noted on RG47-0009 & RG47-0010 and forms placed in job pack?
Job Comments: (Please refer to RG33-0043 for documents turned over to CO Operations)
Service Supplier Company |  |  |  |  | 0 | [5 empty] | Date
Installer Printed Name |  |  |  |  | 0 | [5 empty] | Telephone |  | 0
Installer Signature
For Qwest Use Only
This is: |  |  |  |  | Accepted |  |  | Not Accepted
If NOT Accepted, Reasons:
Operations Representative Printed Name | [6 empty] | 0 |  |  |  |  | Date
Operations Representative Signature | [11 empty] | Telephone |  | 0
Note on Q25: Qwest: Fill in all blocks with an Y, N or NA

## RG47-0004 JIM
Job Information Memorandum
RG47-0004
Date
City, State and Zip | [5 empty] | Office | [7 empty] | BVAPP# |  |  | JIM No.
0 | [5 empty] | 0 | [7 empty] | 0
Service Supplier Company Name
0
Subject
Spec. Item Number
Confirming Telephone Call
From Installer | 0 |  |  |  | To Engineer |  | 0 | [7 empty] | Date
Drawing Change Req | [7 empty] | Job Cost Affected
|  | Yes | No | [5 empty] | Yes |  |  | No
Additional Material Req | [7 empty] | New DWP release req
|  | Yes | No | [5 empty] | Yes |  |  | No
Problem Description
Suggested Remedy
[9 empty] | Total Hours: |  |  |  |  | Total Cost:
Effect on Job Completion Date
Submitted By: | [10 empty] | Telephone No.
Address | [10 empty] | Email Address
|  |  |  | State | [5 empty] | Zip Code

## RG47-0005 General MOP
|  | GENERAL Method of Procedure | [6 empty] | RG 47-0005
|  | COE Installation / Removal / Modification | [6 empty] | (9/04)
Service Assurance Contact Numbers:
800-830-0722 NROC & Alarm Center |  |  |  |  | 800-341-8188 Switch/Sw Pwr.
800-258-8144 Net Facility Center |  |  |  |  | 800-879-1200 Net Management Ctr.
Service Assurance Power Contact No.: 1-800-713-3666
City, State | 0 | Office | 0 | Office Location | 0 | Phone
List Days and Hours of Operation |  |  |  | Start Date | 0 | Completion Date | 0
BVAPP | 0 | JOB ID | 0 | WFA# (if applicable) | 0 | Supplier/Vendor Name | 0
System Type (Refer to RG47-0162 for Power Switch Detailed MOPs) Switch | [5 empty] | Type
Toll |  | Collo |  | Fiber |  | Real Estate
DSL |  | Radio |  | Power |  | Other
Review the steps listed and place Y, N or NA in the appropriate box for the job. Work should not begin until this form has been reviewed and signed by QWEST and supplier representatives. All information must comply with QWEST Technical Publication 77350
STEP |  |  | DESCRIPTION |  |  |  | CO Ops | Installation
1 | A signed Method of procedure (MOP) shall be on site, reviewed and posted. The Question your Work Policy and Have You Considered Checklist has been reviewed.
2 | Have you reviewed the Qwest Supplier Expectations: Access & Security Chapter 2.2 Safety Chapter 2.4, Combustibles Chapter 2.6 TP 77350 on site and available?
3 | All tools and material will be staged/stored at __________________________________________(list location)
4 | The Design Work Package (DWP) is on site and deemed feasible. All assignments are correct, ie. AC and DC Power systems, Grounding, Signal, Synchronization, DS0, DS1, DS3 Fiber and Alarm or Design Engineer has been contacted to correct per field conditions.
5 | All cable racks are sufficient and of the correct type. Cable routes, including entrances to the job associated equipment frames, are available and unimpeded.
6 | The material will be inventoried for correct quantities and types. Any Bill of Material (BOM) shortages will be identified, ordered and set with acceptable delivery dates for on time job completion.
7 | A separate Detail MOP will be completed for all work performed on live equipment whether presently in service or not. This includes work on equipment in an area where potential hazards exist. (A job order may have a number of Detail MOPs. Please see Tech pub 77350 15.3.1)
8 | Alarms will be verified, tested or non-test tagged attached to network element.
9 | Office drawings will be marked to reflect current office conditions.
10 | Applicable job papers, specs, documents, and parts will be signed over to QWEST representative.
11 | Surplus materials and supplier tools will be removed from the job site upon job completion.
12 | AC outlets and equipment lighting have been correctly engineered and provisioned as required.
13 | Real Estate items are complete, ie. Collocation cages, cable holes and other associated building changes.
14 | All material and engineering issues will be escalated to the WMC or Quality Auditor for the area.
JOB DESCRIPTION - please attach an additional piece of paper if necessary |  |  |  |  | FPIN PNAR |  | PNAR | 0
0
EQUIPMENT LOCATION |  |  |  | ALARM
POWER |  |  |  | AI X.25
DSX-1 |  |  |  | TIMING
DSX-3 |  |  |  | FIBER
MDF |  |  |  | MISC
The undersigned approved the procedures herein described as complete, whether a general or detailed procedure. No changes shall be made without approval of both the QWEST Central Office Operations representative and the Installation Supplier Representative or Contract agent.
Name (print & Signature) |  |  | Title | Contact Numbers
Person Performing/In Charge of Work (Required) |  |  |  | 24Hr Emergency Contact Number |  |  | Date
0 |  |  |  | 0
Real Estate or Service Supplier Representative |  |  | (Required) | Phone |  |  | Date
0 |  |  |  | 0
C O Operations Manager or Design Representative |  |  | (Required) | Phone |  |  | Date
0 |  |  |  | 0
Central Office Operations ON CALL Support Technician |  |  |  | Phone |  |  | Date

## RG47-0005 CLEC General MOP
|  | CLEC GENERAL Method of Procedure | [6 empty] | RG 47-0005
|  | COE Installation / Removal / Modification | [6 empty] | (2/06)
Service Assurance Contact Numbers:
800-830-0722 NROC & Alarm Center |  |  |  |  | 800-341-8188 Switch/Sw Pwr.
800-258-8144 Net Facility Center |  |  |  |  | 800-879-1200 Net Management Ctr.
Service Assurance Power Contact No.: 1-800-713-3666
City, State | 0 | Office | 0 | Office Location | 0 | Phone
List Days and Hours of Operation |  |  |  | Start Date | 0 | Completion Date | 0
BAN |  | JOB ID | 0 | WFA# (if applicable) | 0 | Supplier/Vendor Name | 0
System Type (Refer to RG47-0162 for Power Switch Detailed MOPs) Switch | [5 empty] | Type
Toll |  | Collo |  | Fiber |  | Real Estate
DSL |  | Radio |  | Power |  | Other
Review the steps listed and place Y, N or NA in the appropriate box for the job. Work should not begin until this form has been reviewed and signed by QWEST and supplier representatives. All information must comply with QWEST Technical Publication 77350
STEP |  |  | DESCRIPTION |  |  |  | CO Ops | Installation
1 | A signed Method of procedure (MOP) shall be on site, reviewed and posted. The Question your Work Policy and Have You Considered Checklist has been reviewed.
2 | Have you reviewed the Qwest Supplier Expectations: Access & Security Chapter 2.2 Safety Chapter 2.4, Combustibles Chapter 2.6 TP 77350 on site and available?
3 | All tools and material will be staged/stored at __________________________________________(list location)
4 | The Design Work Package (DWP) is on site and deemed feasible. All assignments are correct, ie. AC and DC Power systems, Grounding, Signal, Synchronization, DS0, DS1, DS3 Fiber and Alarm or Design Engineer has been contacted to correct per field conditions.
5 | All cable racks are sufficient and of the correct type. Cable routes, including entrances to the job associated equipment frames, are available and unimpeded.
6 | The material will be inventoried for correct quantities and types. Any Bill of Material (BOM) shortages will be identified, ordered and set with acceptable delivery dates for on time job completion.
7 | A separate Detail MOP will be completed for all work performed on live equipment whether presently in service or not. This includes work on equipment in an area where potential hazards exist. (A job order may have a number of Detail MOPs. Please see Tech pub 77350 15.3.1)
8 | Alarms will be verified, tested or non-test tagged attached to network element.
9 | Office drawings will be marked to reflect current office conditions.
10 | Applicable job papers, specs, documents, and parts will be signed over to QWEST representative.
11 | Surplus materials and supplier tools will be removed from the job site upon job completion.
12 | AC outlets and equipment lighting have been correctly engineered and provisioned as required.
13 | Real Estate items are complete, ie. Collocation cages, cable holes and other associated building changes.
14 | All material and engineering issues will be escalated to the WMC or Quality Auditor for the area.
JOB DESCRIPTION - please attach an additional piece of paper if necessary |  |  |  |  | FPIN PNAR |  | PNAR | 0
0
EQUIPMENT LOCATION |  |  |  | ALARM
POWER |  |  |  | AI X.25
DSX-1 |  |  |  | TIMING
DSX-3 |  |  |  | FIBER
MDF |  |  |  | MISC
The undersigned approved the procedures herein described as complete, whether a general or detailed procedure. No changes shall be made without approval of both the QWEST Central Office Operations representative and the Installation Supplier Representative or Contract agent.
Name (print & Signature) |  |  | Title | Contact Numbers
Person Performing/In Charge of Work (Required) |  |  |  | 24Hr Emergency Contact Number |  |  | Date
0 |  |  |  | 0
Real Estate or Service Supplier Representative |  |  | (Required) | Phone |  |  | Date
0 |  |  |  | 0
C O Operations Manager or Design Representative |  |  | (Required) | Phone |  |  | Date
0 |  |  |  | 0
Central Office Operations ON CALL Support Technician |  |  |  | Phone |  |  | Date
NOTE: CO OPS REP - UPON COMPLETION OF THIS FORM - FAX TO Work Management Center at 303-707-9082

## RG47-0009 Rpt of Dis
RG47-0009
(9/04)
Report of Equipment Disconnected From Existing Plant
|  |  |  | Date: | Sheet __1____ | of ___1_______
Design Engineer's Name |  |  | Address |  | Partial | Final
0 |  |  | 0
City, State, Zip |  |  | Office | BVAPP# | Job ID
0 |  |  | 0 | 0 | 0
| Quantity | Code | Description | Name of Circuit and Location From Which Disconnected. |  | Date Disconnected
| A | B | C | D |  | E
1
2
3
4
5
6
7
8
9
10
11
12
13
14
Service Supplier Representative |  |  |  | * Note complete form and place in job package for auditing
purposes.
Note on G23: Qwest: date form is completed
Note on I29: Qwest: actual date equipment was disconnected

## RG47-0010 Disp of Material
REQUEST FOR DISPOSITION
OF QWEST COMMUNICATIONS MATERIAL
Date
Ship To Location |  |  |  | Street Address | City, State, Zip
Design Engineer's Name |  |  | Design Engineer Fax# | Job Site Address | City, State, Zip
0 |  |  |  | 0 | 0
Engineer Tel No. |  |  | Office CLLI | Office Name | Returned by: |  | Phone/Pager
|  |  | 0 | 0
Job ID |  |  | BVAPP# | RMA Contact Name |  | RMA Contact Phone or Email
0 |  |  | 0
Disposition of Material/Equipment Returned
| Quantity | Part No. | Vendor | Material Description (include all info)* | Reason For Return | RMA | Excess (New) | Reuse (Used) | Salvage/Scrap
| A | B | C | D | E | F | G | H | I
1
2
3
4
5
6
7
8
9
10
* Preferably a highlighted/marked copy of the Bill of Material (BOM) is attached to this form and the Material Description column references the BOM Item Numbers.
Complete all applicable spaces on each row (1-10) to ensure proper disposition of material and proper accounting procedures. Use the codes below to complete
column E and place a checkmark in the appropriate disposition columns for each items (columns F-I)
A - Removed From Existing Plant | D: D - Excess - More Shipped Than Ordered; F: G - Defective - replaced
B - Surplus Ordered by Qwest (New) - Not installed | D: E - Wrong Material Ordered; F: H - Vendor Claim **
C - Surplus Ordered by Qwest (Resue/Excess) - Not installed | D: F- Wrong Material Shipped - Correctly Ordered; F: J - Other reasons (Explain On reverse Side)
** For Vendor Claims must Notify NEP for DEPOT Orders for
material damanged in transportation or at the warehouse.
NOTE TO FORM ORIGINATOR: Fax or email form to: 1) A1 Logistics Customer Service Center Operations (303) 484-5796 or email to RG47@everywarehouse.com
2) RTV/Procurement Group @ 303-707-2795 when Return To Vendor (RTV) requested (Column F)
3) Installation or Construction Group (or to Engineer if originated by Installation or Construction)
4) Retain a copy to in the job package.
To Be Completed By Warehouse
Name of Receiver | D: Phone / Pager; E: Bill of Lading # (Return from Field); I: Date
ATTACH A COPY OF THIS FORM TO EACH BOX BEFORE RETURNING
0
Instructions for completing RG47-0010:
IMPORTANT: EACH BVAPP REQUIRES A NEW FORM TO BE COMPLETED.
EACH SHIPMENT* REQUIRES A NEW FORM TO BE COMPLETED.
1. Complete the top portion of the form with information pertaining to the job, contact information and the location where the material/equipment will be shipped.
2. Input the following information about the material/equipment being returned as follows (each item is recorded on a separate line):
Column A – Input the Unit of Measure (quantity and length)
Column B – Input COE-FM Catalog Part Number (use vendor part number if unavailable)
Column C – Input the Vendor (Manufacturer)
Column D – Input the Material/Equipment Description (or reference the Bill of Material [BOM] item number and attach a highlighted/marked copy of the BOM to the form.)
Column E – Input the appropriate Return Code (list below line 10)
Columns F-I – Only one of these columns is to be marked per item listed on the form:
Column F – Place a checkmark if the material/equipment is to be returned to Vendor (RTV).
This disposition includes material that was sourced from the manufacturer and either arrived broken
and requires replacement, or that is intact but was not used on the job.
Column G – Place a checkmark if the material/equipment is to be sent to the Excess Warehouse.
This disposition is for material that was either sourced from the Excess Warehouse or from Return to Vendor; it was not used and is not being RTV.
Column H – Place a checkmark if the material/equipment is to be sent to the Reuse Warehouse.
This disposition includes material that was either sourced from the Reuse Warehouse or was
removed from existing plant.
Column I – Place a checkmark if the material/equipment is to be salvaged or scrapped. This disposition
includes material that is no longer intact and/or would not be desirable for usage on a future job.
3. Distribute the form (email or fax) as appropriate, using the instructions at bottom of the form. (Most forms will be faxed to 303-484-5796 - warehouse)
* A shipment may be one box, or multiple boxes that are bound together by shrink-wrap, all going to the same location.
Material listed in Column F (Return To Vendor) must have a separate form completed, from material listed in Columns G through I.

## RG47-0013 Ser Degradation Rpt
0
Service Interruption / Service Degradation Report
To: |  |  | Location:
Office | City | State | BVAPP
0 | 0 |  | 0
Time & Date Reported |  | Time & Date Cleared
Type of Equipment |  | MOP Completed/Approved? ____Yes ____No
Description of Service Interruption:
Corrective Action Taken:
Service Supplier Company Name |  | Telephone #
Service Supplier Rep Signature: |  | Date:

## RG47-0157 Test Record
TEST RECORD
DATE
BVAPP | JOB ID |  | CLLI |  | OFFICE NAME |  | City & State
0 | 0 |  | 0 |  | 0 |  | 0
TEST EQUIPMENT USED |  | TYPE CIRCUIT
|  | DS-0 | DS-1 | DS-3 | Alarms | Power | Timing | Fiber
FROM (ex: MDF, RR & Shelf) |  | TO (ex: MDF, RR & Shelf) |  |  |  | LEAD ID / DEFECT TYPE/ CORRECTED (Y/N)
DS-0
DS-1
DS-3
Alarms
Power
Timing
Fiber
INSTALLATION SUPPLIER |  | INSTALLERS NAME(S) (PRINT) |  |  |  | CONTACT NUMBER(S)
0

## AC Elec Quote Form
AC Electrical Work Quote Form
Date | _____________________________________________________________
BVAPP# | 0
Installation Supplier(if not QTI)
Contact
Phone
Contact
Phone
Qwest Engineer/Planner |  | 0
Phone
Qwest Installer |  | 0
| Phone | 0
Description of work performed e.g. placing/removing AC outlets,
lighting, junction boxes, AC runs, etc:
Qwest Central Office |  | 0
(CLLI code and state) |  | __________________________________________________
Estimated Complete Date |  | __________________________________________________
Labor $ | _____________________________________________________________
Hours | _____________________________________________________________
Rate/per hour $ | _____________________________________________________________
Material (if applicable) $ |  | __________________________________________________
Detailed Material List - Please attach a list of Electrical Vendor provided material and Qwest provided
material (if applicable). Included in the Material List needs to be; line item detail, quantities and unit
prices for each part.
FAX TO: 303-707-9151 ATTN: SHERI LONG (PHONE 303-707-5018)

## RG47-0160 CLEC Power
CLEC POWER ASSIGNMENTS
OFFICE |  | 0
BVAPP #: |  | 0 |  | BAN # | 0
CLEC Company & Contact: |  |  |  | Decommission
CLEC Location ID: |  | 0
CLEC COMPANIES LOAD A
FROM-Qwest
BDFB/PBD Location | Shelf | Fuse/Brkr Position | Fuse/Brkr Amps | Cable Length (top to top) | Quantity of runs | Cable Size
CLEC COMPANIES LOAD B
FROM-Qwest
BDFB/PBD Location | Shelf | Fuse/Brkr Position | Fuse/Brkr Amps | Cable Length (top to top) | Quantity of runs | Cable Size
Contacts: Company and/or Name (24 Hour) | [6 empty] | Telephone #
Installation Supplier: |  | 0 |  |  |  |  | 0
Qwest Operations:
Fuses turned over to:

## RG47-0160 CLEC Sync
CLEC SYNC ASSIGNMENTS
OFFICE | 0
BVAPP #: | 0 | BAN # | 0
CLEC Company & Contact: |  | Decommission
CLEC Location ID: | 0
CLEC COMPANIES PRIMARY
FROM-Qwest
Relay Rack Location | Shelf | Slot Position | Port
CLEC COMPANIES SECONDARY
FROM-Qwest
Relay Rack Location | Shelf | Slot Position | Port
Contacts: Company and/or Name (24 Hour) |  |  | Telephone #
Installation Supplier: | 0 |  | 0
Qwest Operations:
For Synch Leads: Termination/Unplugged:

## RG47-0160 CLEC DSO
DSO Circuits
Office |  | 0
BVAPP #: |  | 0 |  |  | BAN # | 0
CLEC Company & Contact: |  |  |  |  | Decommission
CLEC Location ID: |  | 0
Cable Designation |  | DSO Vertical Location MDF/ICDF |  | Pair Count | Comments/Cable Slack (for decom only) | Cable Mined? Y/N (for decomm only)
DSO LINE SHARING ONLY (Data Only)
Cable Designation | DSO Vertical Location MDF/ICDF |  | Pair Count | Splitter Location (RR/Shelf or MDF/Block Location | Comments/Cable Slack (for decom only | Cable Mined? Y/N (for decomm only)

## RG47-0160 CLEC DS1
DS1 Circuits
Office |  | 0
BVAPP #: |  | 0 |  | BAN # | 0
CLEC Company & Contact: |  |  |  | Decommission
CLEC Location ID: |  | 0
Cable Designation | Circuits Cable Count | RR | Panel | Jacks | Cable Slack Length (for decom only) | Cable Mined? Y/N (for decom only)
CLEC Relay Rack Location:

## RG47-0160 CLEC DS3
DS3 Circuits
Office |  | 0
BVAPP #: |  | 0 |  | BAN # | 0
CLEC Company & Contact: |  |  |  | Decommission
CLEC Location ID: |  | 0
Cable Designation | Circuits Cable Count | RR | Panel | Jacks | Cable Slack Length (for decom only) | Cable Mined? Y/N (for decom only)
CLEC Relay Rack Location:

## RG47-0160 CLEC Fiber
CABLES FROM Qwest fiber bay to clec equipment
Office |  | 0
BVAPP #: |  | 0 |  | BAN # | 0
CLEC Company & Contact: |  |  |  | Decommission
CLEC Location ID: |  | 0
Cable Designation | Circuits Cable Count | FDF RR | Panel | Ports | Cable Slack Length (for decom only) | Cable Mined? Y/N (for decom only)
CLEC Relay Rack Location:

## RG47-0161 Quality Checklist
BVAPP # | CLLI CODE:
0 | 0
ENGINEER: | ENGINEER RC CODE:
0 | 0
ITEM TO CHECK | CORRECT? (NA, Y, N) | REMARKS
IRON -
1. Stanchion / Support per standards and configuration? 3.1.7, 3.13.6
2. Cut even and filed smooth? 3.13
- cut ends painted? 3.13.4
3. Bolts and nuts secured? 3.5
4. Lock washers in EQ Heavy areas? 3.9.2
5. Alignment correct? 3.13
6. Finish Clip / Cap in place? 3.4, 3.6
7. Splices / Clamps correct? 3.9.3
8. Cable rack labeled? 8.17
9. Other
BAY -
1. Top support - 2 supports bays, 4 supports cabinets? 3.12.2
2. Preloaded bays are wired correctly, within standards, and match front equipment drawings? 3.13.1
3. Bay ground is correct type and guage, crimped and connected correctly with star washers? 11.3
4. Bay label correct (RG47-0130 or RG47-0131)? 8.1
5. RR designation per standards and configuration? 8.3.1
6. Anchors torqued & Indicators in place or note in job log? 3.21
7. Molding / Dust shield attached? 77351 Chapter 2, Anchoring 2.5.6
8. End shield, end guards (If applicable)? 3.12.7
9. End of aisle labeled (both ends)? 8.3.6
10. AC outlets/lighting installed per standard ? 9.1
11. AC outlets/lighting labeled with fuse box and fuse position? 8.7.1 & 8.7.2
12. Other
EQUIPMENT -
1. Location / Alignment (per Floor Plan, aisle spacing F&R, guards req'd)? 3.16.1
2. Bolts, nuts, screws tightened? 3.5
3. Correct amount of supports? 3.16.2
4. Grounding (chassis/frame) of correct type and guage, crimped and properly connected with star washers? 11.1.8
5. Shelf / Equipment labeling correct per standards and configuration, (ie F/E drawing, RG47-0130) 8.3.
6. Other
CABLE INSTALLATION POINT TO POINT - (Maintenance slack loop not to exceed 4 feet. 5.1)
- DSO -
1. Type & gauge correct? Per DWP and standards
2. Termination location correct both ends? Per DWP
3. Routing correct? 5.1
4. Protection of wire? 5.4
5. Spliced per standard? 5.13
6. Connections
- amphenols seated correctly and secured? 7.3
- wire wraps correct? 7.7
7. Securing : -
- cable lacing secure & correct? 5.5
8. MDF and Blocks labeled correctly? 8.5
9. Shields/Drain leads correct? 7.7
10. Bending radius correct? 5.3
11. Tested? 2.8
12. Other
- DS1 -
1. Type & gauge correct? Per DWP and standards
2. Termination location correct both ends? Per DWP
3. Routing correct? 5.1
4. Protection of wire? 5.4
5. Spliced per standard? 5.13
6. Connections:
- amphenols seated correctly and secured? 7.3
- wire wraps correct? 7.7
7. Securing
- cable lacing secure & correct? 5.5
- Shelf/panel labeled correctly? 8.3
8. Shields/Drain leads correct? 7.7
9. Bending radius correct? 5.3
10. Tested? 2.8
11. Other
- DS3 -
1. Type & gauge correct? Per DWP and standards
2. Termination location correct both ends? Per DWP
3. Routing / Segregation correct? 5.1
4. Cable lacing secure & correct? 5.5
5. Protection of wire? 5.4
6. All labeling correct? 8.3, 8.4
7. BNC / LCC's crimped correctly and installed per standard? 7.2
8. Bending radius correct? 5.3
9. Tested? 7.2.1
10. Other
- FIBER -
1. Type & gauge correct? Per DWP and standards
2. Termination location correct both ends? Per DWP
3. Terminations correctly seated at one or both ends? 7.9
4. Routing correct? 5.1
5. Protection of fiber? 5.10.4
6. Cable lacing secure & correct? 5.10
7. 12 strands or less in trough? (OFNR/P cable) 5.10.10
- 12 strands or more on fiber rack? (OFNR/P cable only) 5.10.10
8. All labeling correct? 8.3, 8.4
9. Bending radius correct? 5.10.6, 5.10.7
10. Slack limits and sotrage adhered to? 5.10.2
11. Tested? 7.9.1
12. Other
- TIMING -
1. Type & gauge correct? Per DWP and standards
2. Termination location correct both ends? Per DWP
3. Leads correctly terminated at both ends. *Note: Shield grounds shall be terminated at ONLY one end unless specifically directed otherwise? 7.7
4. Routing correct? 5.1
5. Protection of wire? 5.4
6. Cable lacing secure & correct? 5.5
7. All labeling correct? 8.4
8. Bending radius correct? 5.3
9. Completed in maintenance window? 2.9.1
10. Tested? 2.8
11. Other
- ALARMS -
1. Type & gauge correct? Per DWP and standards
2. Termination location correct both ends? Per DWP
3. Routing correct? 5.1
4. Protection of wire? 5.4
5. Cable lacing secure & correct? 5.5
6. Connections correct at both ends? 7.3, 7.7
7. Bending radius correct? 5.3
8. All labeling correct? 2.7.1.1, 8.4
9. Alarm record book completed? 2.7.1.1
10. Tested with NMA? 2.7
11. Other
- POWER CABLE -
1. Type & gauge correct? Per DWP and standards
2. Termination location correct both ends? Per DWP
3. Terminations properly crimped and connected at both ends? 9.6
4. Routing correct? 5.1. 9.2
5. Protection of wire? 5.4
6. Bending radius correct? 5.3
7. Supported & secured correctly? 5.5, 9.2.3
8. Power/return fiber tags attached and labeled both ends? 8.11
9. H-taps crimped correctly, taped, cover applied and tied with twine? 9.6.8
10. No-ox applied on connections & fuses? 9.6.4
11. Power Cables banded together in panned rack? 9.2.3
12. Proper voltage and polarity verified and tested? 2.8
13. Completed in maintenance window? 2.9.1
14. Other
BDFB or POWERBOARD -
1. Fuse location correct? Per DWP and standards
2. All labeling correct? 8.10
3. Completed in maintenance window? 2.9.1
4. Other
MISC. FUSE PANEL -
1. Fuse location and size correct? Per DWP and Standards
2. Alarm Fuse Indicator Pin? 8.9.1.2
3. All labeling correct (ie - 48V, shelf label)? 8.10.5
4. Fuse Book has shelf, amp and RR? 8.9
5. If service affecting, completed in maintenance window? 2.9.1
6. Other
CABLEHOLES / FIRESTOPPING -
1. Closure sealed properly? 4, 3M standards
2. Tagged and signed properly? 4.3
3. Location designated top/bottom? 4.4
4. Other
MISC. ENVIRONMENT -
1. Trash removal completed? 2.3.10
2. Bill of lading filled out? 14.2
3. Hazardous material disposal arranged? (Chapter 12)
6. Work area protection? 2.3.6
7. MOP's/Job papers removed from equipment and walls? 2.3.10
8. Foreign Object Ground tested?
If so, what was the reading _______ 1st test __________2nd test
9. Other
DOCUMENTATION -
1. Records/Drawings, installer marked shall be noted 8.18.4
* copy at site?
* copy sent to WMC?
- RED - 8.18.1
All equipment additions
All relocations
All assignment changes
Record title box changes & quantities
- YELLOW - 8.18.2
All equipment being removed from Qwest facility.
If frame numbers, quantities, assignments, change, highlight old numbers
- GREEN - 8.18.3
All "record only" changes
New information regarding existing COE configurations
2. Engineer notified of any & all changes? 2.1.10
* Put note in job log that engineer was notified of changes and date recorded. *
3. MOP's (With start and finish time/date and all relay racks touched). Chp 15
4. JIM's - Chp 13
5. Test Record RG47-0157 - Chp 13
6. Document & Material Disposition Form RG33-0043 - Chp 13
7. Job log RG41-0046 - Chp 13
8. ICN RG47-0002 - Chp 13
9. Most recent release of DWP - Chp 13
10. NMA # on ICN , Job Log, and Installation assignment and Capacity sheet RG41-0170 2.7.2.1
11. PNAR # on ICN? 14.9.6, 15.9
12. Other
COLLOCATION ONLY - CHAPTER 16
1. CLEC Area
- floor taped (if cageless)? Per DWP
- cage built? 16.1.4 and Per DWP
- cage grounded? 16.4.2
- bays labeled? 16.3.2
2. CLEC Provisioning Forms? 14.17, 16.6.1
3. Material Disposition Forms? 14.3
4. Cable slack to required lengths? Per DWP
5. CLEC CLLI code ,floor number,cable name and cable count tagged on cables and labeled on equip.? 16.3.1
6. Cable secured to rack or fence? 16.5.3
7. Lockout tagout on power source? 8.19.5
8. IFB Feed Terminal/NID exist? Per DWP
9. Bay Mounted Line Sharing Splitter Cards SEATED? Per DWP
10. Other
Collocation-Outward Augment (Decommission, Power Reduction, all other removal work)
1. Cables secured, coiled, or tied to rack if reusable? 16.5.3
2. Cables labeled with 2 "Collocation Spare (For Reuse) tags" 1 for each end if reusable? Estimated slack cable footages on tag? 16.5.2
3. All blocks stenciled & labeled if reusable? 8.19.6
4. Power cabling removed from source, tagged and coiled and secured near source for future reuse? 16.5.2
5. Power fuses removed and circuits breakers deactivated and stenciled as spare? 16.5.2
6. Identifying tags attached to colo area or cage (CLEC provisioning forms)? 14.17
7. Yellow or white tape with black lettering used when no place for tags? 8.19.16
8. Is CLEC equipment removed from CLEC site? (Physical) 16.5.2
9. Is CLEC site condition restored (i.e. floors, holes, A/C, stantions, etc.)? 2.3.10, 2.3.13
10. Has Virtual Equipment been removed and delivered to SICM? 16.5.1 and Per DWP
11. Has fuse position been tagged if reserved? 16.5.1
12. Cable measurements sent to engineer? Per DWP
13. CLEC Name removed from all labeling? 8.19.6
14. CLEC Sheets complete (one copy in job pkg., one copy in folder hung on cables)? 16.5.1 and Per DWP
15. Other
Form Completed by: | Date: | Title:
THIS SECTION TO BE FILLED OUT BY STATE INTERCONNECT MANAGER (SICM) ONLY
CLEC FINAL HANDOFF
1. Verify final payment
2. Schedule handoff (SICM, ATR, RE, COM & CLEC)
3. Review access policies
4. Verify card reader
5. Designate CLEC access location
6. Reinforce cell phone policy
7. Reinforce 77350 Standards
- MOP requirement
- identify staging area/masonite policy
- grounding requirements
8. Provide keys/obtain receipt
9. Provide COM phone & pager
10. Provide emergency and maintenance phone numbers
11. Provide tech pub URL location
12. Provide CLEC Provisioning Forms
- provide all detailed data necessary
- label cable ends
13. Verify fiber jumpers have been placed for shared fiber entrance
14. Express fiber withdrawn from CO? Shared fiber unspliced in POI?
15. Obtain CLEC acceptance/completion form
16. Provide contact information for installation of AC outlets for Cageless Collocation
17. Virtual Decommission - CLEC owned equipment returned to CLEC?
18. Other

## RG47-0162 Detailed MOP
0
|  |  | Detailed | [10 empty] | RG47-0162
|  |  | Method of Procedure | [10 empty] | (12/04)
Service Assurance Contact Numbers:
800-830-0722 NROC & Alarm Center |  |  |  |  | 800-341-8188 Switch/Sw Pwr. * Note for Switch & Switch Pwr DMOPactivity use RG47-0162 (09/03 Rev.1)
800-258-8144 Net Facility Center |  |  |  |  | 800-879-1200 Net Management Ctr.
Service Assurance Power Contact No.: 1-800-713-3666
Start Date: |  |  |  | Start Time: |  |  |  | Completion Date: |  |  |  | Complete Time:
Qwest BVAPP# |  | 0 |  |  | Supplier Order Number: | [5 empty] | System Type:
Central Office Name: |  | 0 |  |  | CLLI: |  | 0 |  |  |  | Date:
Design Engineer: |  | 0 |  |  | Installation Service Supplier: |  | 0 |  |  |  | Service Supplier Rep (Print Name): |  | 0
Qwest Representative Approver (Print Name): |  |  | 0 | [7 empty] | Service Supplier Rep Contact #: |  | 0
Identify equipment to be installed, modified, or removed:
Planned Network Activity Registration Number |  |  | Job Type |  |  | Power |  |  | IOF |  | Other
0
If there is not a CO Operations manager or Qwest representative on site (after DMOP is approved and before beginning work) and/or you suspect that you’ve caused a service interruption, call as indicated: Switch/ Switch Power/ Power: 800-341-8188 option 1. * Note for Switch & Switch Pwr DMOPactivity use RG47-0162 (09/03 Rev.1) Toll/ IOF/ Synchronization/Timing/Other: 800-258-8144
Detailed below are all the steps necessary to explain the work that is to be performed. Steps will be numbered, and appear in the order in which they will occur, with the work operation responsibility indicated by checking the appropriate boxes. Work will not begin until this form has been reviewed and signed by QWEST and Supplier representatives. This form may be duplicated if additional space is required. All information must comply with QWEST Technical Publication 77350 or applicable Qwest Technical Publication.
Have you Considered?
• Added or removed equipment with potential to impact service or working equipment | [5 empty] | • Hazardous materials handling and disposal |  |  |  |  | • Establishing a bridge with the NROC to monitor the office
• Eye wash, battery spill kit, First Aid available | [5 empty] | • Location of spare fuses |  |  |  |  | • Office records/drawings available and corrected
• Equipment Compatibility | [5 empty] | • Before and after tests |  |  |  |  | • Documents referenced in the MOP on-site
• Affected Working Circuits | [5 empty] | • Emergency restoration plans |  |  |  |  | • Back out procedures
• Work area protection | [5 empty] | • All applicable Product Change Notices have been reviewed/applied |  |  |  |  | • Fuse alarm operation
• Special tools/ insulated tools /materials | [5 empty] | • Cables have been metered and traced |  |  |  |  | • Personal Protection Equipment
Question Your Work
# | ITEM | [11 empty] | Date and Initial (Service Supplier)
1 | Prior to commencement of work operation(s), I have requested proper coverage. g CO Operations Representative notified? gHas everyone who needs to know about the impact of this work been notified? | [11 empty] | Yes |  | No
2 | Can I prevent or control service interruptions? | [11 empty] | Yes |  | No
3 | Is this the right time to do this work? Check proper Maintenance Window/time (M-F) Time: (Sa-M) Time: | [11 empty] | Yes |  | No
4 | I am trained and qualified to do this work? | [11 empty] | Yes |  | No
5 | Is the supporting documentation current and error-free to minimize all risks associated with this task? | [11 empty] | Yes |  | No
6 | I have everything I need to quickly restore service if something goes wrong? | [11 empty] | Yes |  | No
| w Step-by-step "backout" procedures | [11 empty] | Yes |  | No
| w Cables tagged for ease or reconnection | [11 empty] | Yes |  | No
| w Spare fuses of the proper amperage for the equipment relevant to this DMOP. | [11 empty] | Yes |  | No
| w The proper material (e.g., lugs, screws/bolts/nuts, connectors, cable/wire, etc.) | [11 empty] | Yes |  | No
7 | I am using the right tools to perform this work. | [11 empty] | Yes |  | No
8 | In the event of a service interruption, I will complete the RG47-0013 and notify:
| w Qwest network Management Center: 800-879-1200 Option 1 | [11 empty] | Yes |  | No
| w Qwest CO Operations | [11 empty] | Yes |  | No
| w My immediate Supervisor | [11 empty] | Yes |  | No
9 | Working equipment that has been deactivated/powered down/removed from service in order to complete these procedures will be placed back in service. | [11 empty] | Yes |  | No
10 | I have identified the locations of essential and/or government circuits such as:
| w 911 | [11 empty] | Yes | No | NA
| w Federal Aviation Administration (FAA) | [11 empty] | Yes | No | NA
| w System Signaling 7 (SS7) | [11 empty] | Yes | No | NA
| I have previously submitted the PNAR and notified NROC, so that they could initiate release requests to ensure proper authorization.* | [11 empty] | Yes | No | NA
| I have ensured that these circuits have been properly identified, labeled, and that the NROC has contacted the appropriate representatives to obtain the proper work release authorization(s). Note: Use the Search Tool http://pas16.uswc.uswest.com/omni/docview.html | [11 empty] | Yes | No | NA
* Required for upgrades/retrofits that do not use the CIA process. The Service Supplier must initiate the PNAR at least 10 days prior to performing the upgrade/retrofit so that the NROC can obtain the releases. * IF YOU ANSWERED "NO" TO ANY OF THE ABOVE -- CALL YOUR SUPERVISOR PRIOR TO JOB START
RESPONSIBILITY
S T E P # | S U P L | Q W E S T | S S P * | DESCRIPTION OF WORK OPERATION
0 | [9 empty] | 0

## RG47-0165 Common Sys Ord Form
|  | Fax order to: | WMC AA- AZ, MT, NM, WY, NE, IA, OR Susan Agostine 303-707-7987 |  |  | Date
|  | 303-707-9673 | WMC AA CO, ND, SD, MN, WA, ID, UT Andrew Noworytta 303-707-5029
City | State | Work Type | BVAPP | BVAPP Ref# | Job ID | ACCT Codes
0 |  |  |  | 0 | 0
Address ID | CLLI code | Engineer's Name | Engineering RC Code | Engineering Company |  | Install Comp Date
0 | 0 | 0 | 0 |  |  | 0
Installation Manager |  | Ordered By | Installer Pager | Installer Phone | Install Company | RFS Date
0 |  | 0 | 0 |  | 0
Ship to:
Special Shipping or Material Staging Instructions (shipping to CO site must be approved by Installation Supervisor or WMC Manager):
Standard shipping method is ground, all other must be approved by departmental Director.
QTY. | PART NUMBER | MANUFACTURER | CATALOG DESCRIPTION |  |  | CONSUMABLE MATERIAL ITEM Y/N
(Mandatory) | (Mandatory) | (Optional) | (Mandatory) |  |  | (Mandatory)

## RG47-0166 Missing Mat Form
JOB SITE MATERIAL INVENTORY FOR MISSING ITEMS
DATE:
BVAPP# | 0
JOB # | 0
OFFICE/CLLI: | 0
INSTALLATION VENDOR: |  | 0
CONTACT NAME: |  | 0
CONTACT NUMBER: |  | 0
Bill of Material Item # | Part # | Description | Quantity
Comments:

## RG47-0168 App Letter of Dev
0
Application for Letter of Deviation
(Completed by the Installation Service Supplier)
. | Issued in rare cases when all othr viable engineering options have been explored and eliminated
. | Used for one-time, site-specific conditions and is documented accordingly.
. | Not valid soley for wholesale or economic concerns.
. | Not used to remedy quality workmanship defects
. | Not to be used to continue non-standard practices that may have bee applied in the past, or
where new standards have superceded the old (i.e., earthquake bracing upgrades due to
seismic zone changes).
. | A Letter of Deviation should be approved prior to the Installation start date, but must be
approved prior to the Installation complete date.
. | All affected Central Office drawing layers must be marked accordingly.
Installation Service Provider:
Provide a detailed description of the rationale for applying for a letter of Deviation
(include: all applicable reference drawings / sketches, safety, environmental, technical,
and service concerns. Identify the exact Qwest AMC, technical documentation or
Technical Publication chapter, and paragraph / section the deviation applies to:
Date of Application:
State: | 0 | Central Office: | 0 | Job Number/BVAPP: | 0
Location within Central Office:
Deviation submitted to Design Engineering Representative:
Name of Application Originator:

## Engineer Feedback form
|  | Please put Y / N / NA |  |  | 1=Needs Improvement 2=Meets Expectations 3=Outstanding
BVAPP | Design Engineer (DE) | Was DWP clear & concise? | Did DE provide sufficient support? | Was DE professional? | DWP/DE Rating | Comments
0 | 0

## REGN 154-004-001RG
REGN 154-004-001RG |  |  | 0
Issue 3, Oct 2006
Exhibit 1
Environmental Equipment Notification - Batteries
This form is to be completed for each battery string installation, removal, and replacement project. To ensure appropriate
permitting, agency notification, and EHS review, this form should be faxed to EHS at 303-992-7111 or may be e-mailed to
QEHS@qwest.com with 30 days of the estimated project date. Questions regarding this form can be directed to the EHS
Department at (303)992-7091
SECTION A - Project Information
Facility
Name: | 0
|  |  |  | CLLI |  |  | Wireless Site
GEO Code: |  | 0 |  | Code: | 0 |  | ID:
Street: | 0
City & State: |  | 0 |  |  |  |  | Zip:
Project
Contact: |  |  |  |  | E-mail:
Phone |  |  |  |  | Fax
Number: |  |  |  |  | Number:
SECTION B - New Batteries
The following information should be noted for each set of batteries to be installed. If more than two types of batteries are to be
installed, submit additional forms as necessary.
Battery Install 1
| Est. Install Date: |  |  | Battery Type: |  | VRLA: |  | Flooded:
| Manufacturer |  |  | Model:
| No. Strings: |  |  | Jars per string:
Location in Buildings:
Battery Install 2
| Est. Install Date: |  |  | Battery Type: |  | VRLA: |  | Flooded:
| Manufacturer |  |  | Model:
| No. Strings: |  |  | Jars per string:
Location in Buildings:
SECTION C - Removed Batteries
The following information should be noted for each set of batteries to be removed. If more than two types of batteries are to be
removed, submit additional forms as necessary.
Battery Removed 1
| Est. Removal Date: |  |  | Battery Type: |  | VRLA: |  | Flooded:
| Manufacturer |  |  | Model:
| No. Strings: |  |  | Jars per string:
Location in Buildings:
Battery Removed 2
| Est. Removal Date: |  |  | Battery Type: |  | VRLA: |  | Flooded:
| Manufacturer |  |  | Model:
| No. Strings: |  |  | Jars per string:
Location in Buildings:
TABLE A
Region |  | States |  |  |  |  | Manager
Northwest |  | OR, WA, CA |  |  |  |  | Tom Pitts
Mountain |  | ID, NM, NV, UT |  |  |  |  | Kevin Robison
Rocky Mountain |  | CO, MT, WY, TX, KS, OK |  |  |  |  | Barb Dowski
Midwest |  | IA, IL, IN, MI, MN, ND, NE, OH, SD, WI |  |  |  |  | Gerard Breen
South |  | AZ |  |  |  |  | John Ferguson
Atlantic |  | CT, DC, DE, FL, GA, MA, MD, ME, NC, NH, NJ, NY, PA, RI, SC, VA, VT, WV, AR, KY, LA, MO, MS, NM, TN |  |  |  |  | Harlan Pincus
Name |  | Title |  | Phone Numbers |  | Address |  | E-mail
Brian Jacobson |  | Senior Environmental Project Manager |  | 303-992-7090 Office |  | 1801 California Street |  | brian.jacobson@qwest.com
|  |  |  | 303-992-7111 Fax |  | Suite 1160
|  |  |  | 303-257-8472 Mobile |  | Denver, CO 80202
Gerard Breen |  | Regional Environmental Manager |  | 612-798-2424 Office |  | 300 W 66th |  | gerard.breen@qwest.com
|  | Midwest Region |  | 612-798-2451 Fax
|  | IA, IL, IN, MI, MN, ND, NE, OH, |  | 612-275-8352 Mobile |  | Richfield, MN 55423
|  | SD, WI |  | 877-548-1026 Pager
Barb Dowski |  | Regional Environmental Manager |  | 303-441-6159 Office |  | 1855 S. Flatiron Ct. |  | barb.dowski@qwest.com
|  | Rocky Mountain Region |  | 303-441-6064 Fax |  | Boulder, CO. 80301
|  | CO, MT, UT, WY, TX, KS |  | 303-257-8512 Mobile
877-703-9697 Pager
John Ferguson |  | Regional Environmental Manager |  | 602-235-1484 Office |  | 3640 E Indian School Rd |  | john.ferguson@qwest.com
|  | South Region |  | 602-235-3311 Fax
|  | AZ |  | 602-576-3668 Mobile |  | Phoenix, AZ 85018
877 867 9631 Pager
Harlan Pincus |  | Regional Environmental Manager |  | 914-686-7952 Office |  | 55 Church Street |  | harlan.pincus@qwest.com
|  | Atlantic Region |  | 914-686-7963 Fax |  | First Floor
|  | CT, DC, DE, FL, GA, MA, MD, ME, NC, NH, NJ, NY, PA, RI, SC, |  | 914-420-2528 Mobile |  | White Plains, NY 10601
|  | VA, VT, WV, AR, KY, KA, MO, MS, NM, TN |  | 877-867-9710 Pager
Kevin Robison |  | Regional Environmental Manager |  | 801-237-3006 Office |  | 250 E 2nd S |  | kevin.robison@qwest.com
|  | Northwest Region |  | 801-237-5334 Fax |  | Salt Lake City, UT 84111
|  | ID, NM, UT, NV |  | 801-598-3020 Mobile
877-441-1199 Pager
Robin Seguin |  | Environmental Project Manager |  | 303992-7091 Office |  | 1801 California Street |  | robin.seguin@qwest.com
|  |  |  | 303-992-7111 Fax |  | Suite 1160
|  |  |  | 720-209-3540 Mobile |  | Denver, CO 80202
Tom Pitts |  | Regional Environmental Manager |  | 206-346-7532 Office |  | 1600 7th Ave. |  | thomas.pitts@qwest.com
|  | Northwest Region |  | 206-345-8705 Fax |  | Room 2708
|  | OR, WA, CA |  | 206-271-7532 Mobile |  | Seattle, WA 98191
877-871-1680 Pager

## Form 820 Gen Tst Chklst
FORM 820
GENERIC TEST & ACCEPTANCE CHECKLIST
Site: | 0 | BVAPP: |  | 0
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM: |  |  |  | YES | NO
Equipment Verification
Frames located per floor plan
Installed per drawings
Equipment is what was ordered
Equipment options are correct
Spare equipment provided per ordering spec (if applicable)
Power feed to equipment checked
Workmanship
Frame alignment and equipment mounting
Relay rack numbering
Wiring and cabling
Equipment numbering and lettering
Cable openings sealed
Cable racks and other ironwork
Power and fusing (spare fuses available also)
Performance Tests
Tests per recommended equipment manual
Tests per Test & Acceptance package sent out with job (contact the Engineer if no such package sent)
Documentation
"As-built" drawings sent back to engineering
Replacement drawings
Initial battery charge reports (if applicable)
Equipment manuals received
Original test results retained
Alarms
Affected alarms tested prior to work start
Local and audible alarms (as applicable) tested prior to work start
Remote alarms installed and tested with NROC Alarm Center (800-713-3666)
Name of NROC Center Contact with whom alarms were tested:
Other
Comments (all No answers must be commented on)

## Form 821A Pwr Rm Lhtg chklst
FORM 821A
POWER ROOM LIGHTING TEST & ACCEPTANCE CHECKLIST
Site: | 0 | BVAPP: |  | 0
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM: |  |  |  | YES | NO
1. Lighting provided in the power areas is adequate, and located in accordance with the SITE: record lighting plan drawing
2, As a minimum, emergency and task/stumble lighting is available in stairwells, over the "power board", over the engine control panel and AC transfer switch, over the AC switchgear, and in the engine room
3. Emergency and task/stumble lighting works
4. Feeding fuse/breaker positions and emergency and task/stumble lighting fixtures are properly stenciled as to the equipment they feed or where they are fed from
Test & Acceptance should be performed with the installer on site. Note below all problems they fix
Comments (all No answers must be commented on)

## Form 821B Alm Tst Chklst
FORM 821 B
ALARM AND/OR POWER MONITOR/CONTROLLER (PSMC)
TEST & ACCEPTANCE CHECKLIST
Site: | 0 | BVAPP: | 0
Associated Power Plant: |  | ANCR#:
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM: |  |  |  | YES | NO
1. Complete copy of suppliers' manuals and drawings available on site
2. Verify accuracy of the database, and ensure an electronic backup is made where applicable
3. Verify that analog channel readings are within 1% of the values measured by plant meters or by technician's hand-held meter
4. Bring in each binary alarm associated with this monitor (or other alarming device) and verify that technicians in Power NROC (800-713-3666) receive the alarm over NMA
A. There is local indication of the alarm on the monitor, if monitor is capable of this function
B. If monitor is capable and equipped, verify the difference between Minor Rectifier Fail (1 rectifier), and Major Rectifier Fail (2 or more rectifiers failed)
5. Bring in binary alarms associated with the threshold settings of analog points (e.g., low voltage, etc.), and ensure that these alarms report locally on monitor and over NMA
A. Analog points' binary thresholds are set properly (according to REGN 154-103-001)
6. If monitor is controlling High Voltage Shutdown (HVSD) verify proper operation
7. Ensure that all binary, analog, & control points requested on engineering job were provided, & ensure that there is a record left in office on paper and/or on disk of the assignments
8. If monitor is capable and equipped, verify the difference between Minor Converter Fail (1 converter), and Major Converter Fail (2 or more converters failed)
9. Verify security levels (e.g., different passwords), and dial-back numbers (if applicable)
10. System reboots properly after being turned off/on
11. Verify through NROC Center or NMA database group continuity of X.25 link where applicable
12. When monitor is equipped with control functions, verify proper operation of these functions (e.g., rectifier shutdown/restart, engine start/stop, etc.)
13. Verify that laptop can communicate with monitor over RS-232 port
14. Verify communication with unit over a dial-up
Test & Acceptance should be performed with the installer on site. Note below all problems they fix
NOTE: Use supplier, Bellcore, and Qwest documentation as a guide to performing the tasks above. NOTE: When testing alarms and functions, be sure not to interrupt service unless done during the Maintenance Window and with notification to appropriate personnel
Comments (all No answers must be commented on)

## Form 821C BDFB PBD Chklst
FORM 821 C
BDFB, POWER BOARD, OR FUSE PANEL
TEST & ACCEPTANCE CHECKLIST
Site: | 0 | BVAPP: |  | 0
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM: |  |  |  | YES | NO
1. Proper equipment was ordered and is sized appropriately for the application
2. Verify proper load bus arrangements
3. Verify proper return bus options
4. Verify accuracy & proper operation of the digital or analog meters & current shunts
5. Test fuse alarms for proper operation and continuity to NROC (Note: BDFBs and other secondary fuse panels are not monitored by the Power NROC group, but by the groups who monitor the equipment served by these secondary protection devices)
6. Verify proper placement, anchoring, and stenciling of the bay(s) and/or shelves
7. Ensure that all fuse/breaker assignments are properly marked/stenciled for the loads they feed, and that all incoming and outgoing cables are properly tagged
8. Verify proper connections of wires/cables to the fuse distribution, ground, and battery return busses/connections
9. Verify proper cable routing
10. Verify proper frame and central office grounding
11. Ensure that BDFBs are equipped with a sticker(s) specifying the maximum feeder load (50% of the protector size) for each feeder
Test & Acceptance should be performed with the installer on site. Note below all problems they fix
NOTE: Use supplier documentation as a guide to performing the tasks above. NOTE: Work on a Power Board or BDBF has the potential to interrupt service. Service shall not be interrupted when installing primary or secondary distribution panels. Cutover of a BDFB or Power Board should probably occur during the Maintenance Window if the power plant is already up and supporting loads.
Comments (all No answers must be commented on — use the back of this form if necessary)

## Form 822 Battery Tst chklst
FORM 822
BATTERIES & BATTERY STANDS TEST & ACCEPTANCE CHECKLIST
Site: | 0 | BVAPP: |  | 0
Associated Power Plant: |  | Battery String #:
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM: |  |  |  | YES | NO
1. Battery stands and batteries are stenciled or identified with a minimum of installation and/or manufacturing date (on batteries), string numbers/letters, and cell numbers.
2. Batteries and connectors are free of the following defects.
A. Cases crazed, cracked, bulged, corroded, or leaking
B. Level indicators stuck or missing
C. Cover or post rise, and/or post corrosion
D. Excessive positive plate growth or strap growth
E. Excessive plate bowing or cracking
F. Excessive needle growth
G. Lead-sulfate crystals (this should be checked after batteries have received their full initial charge)
3. Electrolyte level is proper, and limits for electrolyte level are marked on the batteries.
4. Proper vent and filler caps or funnels are installed, and flame arrestors are equipped with dust covers.
5. Battery records/logs and any manufacturer documentation are on-site and easily accessible. The Storage Battery report (RG47-0001) should have been filled out by the installation vendor.
6. Neutralizing agents and protective equipment are available nearby for use as required in the battery area (eyewash, baking soda or equivalent, rubber gloves, goggles, rubber apron).
7. Thermometers, hydrometers, and holders are furnished and mounted as required.
8. Check batteries and intercell connections integrity by placing string on a short 5 minute discharge test into a real load or load box load. (This requirement is optional due to the fact that some battery strings are installed long before they are connected to the real load.) As a minimum attempt to determine if connections were properly tightened with a torque wrench.
9. All voltage readings are within (+-) 0.05 of the float average (e.g., 2.20 V/cell)
10. Spill and disposal procedures are posted near the batteries.
11. Battery stand is braced appropriately for earthquake zone in which site is located.
Test & Acceptance should be performed with the installer on site. Note below all problems they fix.
Comments (all No answers must be commented on)

## Form 823A Rect Tst Chklst
Form 823A
RECTIFIER TEST & ACCEPTANCE CHECKLIST
Site: | 0 | BVAPP: | 0
Rectifier #’s |  | Associated Power Plant
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM: |  |  | YES | NO
1. Rectifiers are properly assembled, installed, and stenciled or identified
2. Correct type & capacity fuses are provided, & all fuses are clean & properly installed
3. AC power connections are properly made. Ensure proper transformer taps and phase rotation where applicable
4. Ensure that correct rectifier (size, type, AC input, etc.) was ordered, including correct wiring or apparatus options
5. Rectifiers operate per individual operation tests, and basic operational features work
6. Plant meters are accurate and properly adjusted
7. Alarm settings are adjusted to requirements, and proper alarm signals are transmitted (ensure alarms reach the NROC Center)
8. Current limiting and partial load features of units are set and adjusted properly
9. High voltage shutdown (HVSD) feature operates properly, and all other DIP switches, potentiometers, and other options are properly set, including alarm thresholds
10. Outputs of all units are stable (non-hunting, except for load sharing variations), & rectifier float voltages are properly set for battery type (see REGN 154-103-001) & load sharing
11. Test rectifier fail alarms for continuity to the NROC Center
12. Simulate an AC power failure to verify that the units' auto-restart capability and current walk-in feature operate properly when AC power is restored. Ensure also that alarms clear and that the units return to float voltage
13. All rectifiers are capable of operating, regulating, and current limiting at full load
14. Ensure AC fuse panel(s) feeding rectifiers have adequate spare capacity. If not, notify Real Estate
15. For multi-phase fed rectifiers, verify appropriate operation or shutdown during phase failure
16. Ensure proper selection and routing of rectifier control cables to plant controller
17. Ensure rectifier frames are properly grounded & that battery return cables are properly grounded & sized, dependent on whether plant is integrated, isolated, or combined
18. Ensure rectifier DC output cables are properly installed, & sized according to Tech Pub 77385 (for 200 and 400 Amp rectifiers), or manufacturers’ recommendations (all other sizes)
19. Ensure that there is adequate ventilation & heat dissipation so rectifier will not overheat

## Form 823B Pwr-Batt Tst Chklst
Form 823B
POWER/BATTERY PLANT TEST & ACCEPTANCE CHECKLIST
Site: | 0 | BVAPP: | 0
Power Plant: |  | Location:
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM |  |  | YES | NO
1. All battery distribution cables are of correct size and type, and properly terminated
2. All equipment of control and distribution bays are correctly stenciled or identified
3. All control circuit, charge, and discharge fuses and/or circuit breakers are of the correct type and 4. capacity, and located as shown on the drawings
4. Alarm fuse positions are equipped with correct fuses, and fuse and circuit breakers are properly designated as to the equipment they serve
5. Verify alarm operation, both locally, and to the NROC Center
6. All DC meters are calibrated and properly adjusted
7. All fuses are tight in their respective fuse holders, and fuses and circuit breakers are free of excessive heat
8. The battery float voltage is correct (check after meter calibration, and initial charging of the batteries)
9. The voltage alarm settings are correct per REGN 154-103-001
10. Spare fuses are provided, and properly located and designated, on or near the battery plant
11. If LVD is used (use only where required, such as with a DMS®10 switch), ensure setting is -43.25 V or less.
Test & Acceptance should be performed with the installer on site. Note below all problems they fix
Comments (all No answers must be commented on)

## Form 824A Cnvt Plnt tst chklst
Form 824A
CONVERTER PLANT TEST & ACCEPTANCE CHECKLIST
Site: | 0 | BVAPP: | 0
Associated Power Plant: |  | Location:
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM |  |  | YES | NO
1. The converter plant is properly assembled and installed (including properly made electrical connections, and stenciled or identified
2. The input and output fuses are the correct type and capacity
3. The discharge fuse alarms are operative, and connected properly, and spare fuses are available
4. The voltage alarm levels are properly adjusted to specified limits
5. All alarms function properly, and are received by the NROC Center
6. High voltage shutdown (HVSD) feature operates properly
7. The converter plant meters are accurate, and properly adjusted, and all other LEDs or other indicators work properly
8. The output voltage is adjusted within the specified limits, and can be accurately read from the test jacks
9. The output current limit is properly set, as well as any other options set through DIP switches or potentiometers
10. Verify that the converter plant functions properly under load for at least 30 minutes, and that there are no problems if the converters are switched on and off.
Test & Acceptance should be performed with the installer on site. Note below all problems they fix
NOTE: When testing alarms and functions, be sure not to interrupt service unless done during off hours and with notification to appropriate personnel
Comments (all No answers must be commented on)

## Form 824B Res Ring Plnt Chklst
Form 824B
RESIDUAL RING PLANT TEST & ACCEPTANCE CHECKLIST
Site: | 0 | BVAPP: | 0
Associated Power Plant: |  | Location:
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM |  |  | YES | NO
1. The ringing plant is properly assembled, installed, and stenciled or identified
2. Ringing plant fusing is in agreement with site drawings
3. All alarms operate properly, including transfer alarms (ensure alarms reach NROC center)
4. The transfer feature operates automatically when a power failure occurs (for units when Ring Generator 1 is AC powered), or if Ring Generator 1 fails. (This transfer also applies to those sites equipped with interruptors besides the ring generators)
5. If equipped, the transfer feature operates properly by manual or test transfer methods
6. All voltages, tone levels, and frequencies are within specified limits
7. If meters are provided, they are accurate, and within adjustments
Test & Acceptance should be performed with the installer on site. Note below all problems they fix
Comments (all No answers must be commented on)

## For 825A Inverter Tst Chklst
Form 825A
INVERTER TEST & ACCEPTANCE CHECKLIST
Site: | 0 | BVAPP: | 0
Associated Power Plant: |  | Location:
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM |  |  | YES | NO
1. The inverter plant is properly assembled and installed (including proper electrical connections), and stenciled or identified
2. Input, output, and alarm fuses are the correct type and capacity, and output distribution is properly sized and connected
3. Simulate an AC power failure. Ensure proper operation and transfer. During outage check output voltage and frequency
4. Verify that plant is capable of operation at full load, in both AC input or DC input modes. (Use a dummy load — e.g., load box — if necessary to fully load the plant)
5. Verify proper operation of maintenance bypass, if equipped
6. Verify proper operation of transfer switch
7. Alarms operate and clear properly (ensure alarms remote to the NROC Center)
8. Verify proper operation of any automatic shutdowns (e.g., low voltage, emerg. stop, etc.)
9. Verify proper operation of all controls and indicators (meters, LEDs, etc.)
10. Ensure that the green wire ground is properly connected
11. Ensure there is adequate room and ventilation around the inverter
Test & Acceptance should be performed with the installer on site. Note below all problems they fix
NOTE: When testing alarms and functions, be sure not to interrupt service unless done during off hours and with notification to appropriate personnel
Comments (all No answers must be commented on)

## Form 825B UPS Tst Chklst
Form 825B
UPS TEST & ACCEPTANCE CHECKLIST
Site: | 0 | BVAPP: | 0
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM |  |  | YES | NO
1. The UPS is properly assembled, installed, and stenciled or identified in accordance with Engineering instructions
2. The correct type and capacity fuses are provided, and all fuses are clean and properly installed
3. AC/DC power connections are made in accordance with Engineering instructions, and in compliance with Qwest 4. 4. Technical Publication 77355
4. Transformer taps are set properly
5. Ensure proper AC phase rotation on the output
6. Plant meters are accurate and properly adjusted
7. Alarm settings are adjusted to requirements, and proper alarm signals are transmitted. Ensure that alarms reach NROC Center
8. Correct wiring or apparatus options provided
9. Current limiting and partial load features of units are set and adjusted per Engineering requirements
10. High voltage shutdown feature operates properly
11. Outputs are stable (non-hunting, except for load sharing variations)
12. Simulate AC power failure to verify unit's auto-switch capability, and that it operates properly when AC power is restored (ensure that alarms clear when AC is restored). Check for proper return to battery float voltage
13. UPS capable of operating at full load
14. Battery chargers are operating at the required output voltage
Test & Acceptance should be performed with the installer on site. Note below all problems they fix
NOTE: Use supplier documentation as a guide to performing the tasks above.
NOTE: When testing alarms and functions, be sure not to interrupt service unless done during off hours and with notification to appropriate personnel
Comments (all No answers must be commented on)
reference Routines EE550 and EE551

## Form 826A Eng Tst Chklst
Form 826A
STANDBY ENGINE TEST & ACCEPTANCE CHECKLIST
Site: | 0 | BVAPP: | 0
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM |  |  | YES | NO
1. Engine-alternators & associated equipment are located according to the floor plan drawings, & are installed according to Engineering request, & are properly sized (e.g., fuel and exhaust system piping & tubing)
2. Engine start batteries and chargers are in good condition, and installed and operating properly
3. Verify start batteries and charger per Forms 822, 823A, manufacturers’ documentation, and TPP below
4. A remote emergency stop switch/button is located outside but near the engine room, & is properly identified
5. Test records, logs, and manufacturer documentation is on site and accessible
6. Before operation, inspect for the obvious, like assembly; fuel or oil leaks; or loose, missing or damaged parts
7. Fuel in main and day tanks is sufficient and free of excess water and other contaminants
8. Oil and coolant levels are sufficient, fluids are contaminant-free, and jacket water heater is operational
9. Engine-alternator operating instructions are posted near the engine, and are clear and easy to use
10. Adequate ear and eye protection is available in the engine room, and adequate warning labels are posted
11. Ensure that engine, engine room metallic parts & lines, and alternator neutral are all grounded per Pub 77355
12. Engine crankcase breather is vented to atmosphere or discharge damper
13. With the engine mfg & the installer present perform a first test of the genset with the engine on a full load bank for 2-4 hrs (preferably run this test on site; however, the test may be done at the mfg’s location with Qwest present to observe). Observe all functions, readings, alarms, etc., & note abnormalities, paying special attention to the following:
A. Water, fuel, and oil temperatures and pressures are within limits
B. Ensure proper operation of the transfer switch
C. Frequency, current, kW, and voltage readings are correct, and within limits
D. Test all alarms during run, both locally and remotely (to Power NROC) for proper operation
E. If provided, rectifier sequencing functions properly
F. Exhaust press. < limits; no exhaust leaks; internal exhaust pipes insulated; 9" min. exhaust clear from combustibles; hot "reachable" parts guarded and/or labeled; exhaust couplings use bolted flanges with gaskets or threaded pipe; has a flex connection to engine & flex supports to allow for expansion/contraction; & end of exhaust stack protected
G. Ensure proper operation of all fuel pumps, and the day tank (where applicable)
H. Intake/exhaust fans/louvers operate (& held open by spring on AC loss), & properly sized per dwgs. (Check proper intake size by seeing if engine room door opens easily). Air intake filters properly installed? (Exhaust fans to be controlled by room thermostat, if separate.) Exhaust positioned so its gasses & heat are not part of intake air.
I. If provided, paralleling functions properly
J. Current load is reasonably balanced between phases
K. All required gauges, meters, and local and remote alarms are present as per Pub 77385
L. Test emergency shutdown
14. Check fluids and fuels after run, and visually inspect for leaks, loose parts, etc.
NOTE: Use supplier documentation, as well as TPP T.AMC.POWR.96.0008 for more complete engine Test and Acceptance
NOTE: When testing alarms and functions, be sure not to interrupt service
Comments (all No answers must be commented on — (Please use the back of this form for comments)

## Form 826B Trans Swt & AC Cklst
Form 826B
TRANSFER SWITCH AND AC SERVICE ENTRANCE
TEST & ACCEPTANCE CHECKLIST
Site: | 0 | BVAPP: | 0
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM |  |  | YES | NO
1. Ensure proper operation of the transfer switch. Simulate an AC failure and return of Commercial AC. Ensure that all timers function properly.
2. If provided, paralleling functions properly and that there are sequencer lights or meters which properly operate if paralleling is to be done manually.
3. Ensure that drawings for the transfer switch are on site.
4. Ensure that a single line-drawing is on site (it may be physically etched or drawn on the AC switchgear)
5. Visually inspect (or thermally with a thermal gun or camera) all connections in the transfer switch and AC service entrance cabinets for tightness.
6. Ensure that the AC loads of the site do not exceed buss bar and breaker capacities in the AC switchgear.
7. Ensure that electrical safety equipment is available for the site: electrical gloves, goggles, and tags/locks for use in lockout/tagout procedures when AC work is being done and possibly fire-retardant Nomex gear.
8. Ensure that AC service entrance has a lightning arrestor and/or surge suppressor properly installed.
9. Ensure that the AC fail is monitored per phase, and that an AC fail alarm properly reports through the alarm systems to the NROC Center.
10. If the site is equipped with a power monitor (PSMC), verify that AC voltage (per phase, line-neutral) and currents (per phase) are monitored and reading properly.
11. Ensure that the power company transformer is adequately sized to handle the site load.
12. Ensure that the AC Service Entrance and Transfer Switch have proper grounding connections per Pub 77355
13. Ensure that there is proper interrupt current rating coordination from the power company transformer down to the PDSCs (e.g., ensure that the K.A.I.C of the service entrance equals or exceeds that of the power company transformer, etc.)
NOTE: Use supplier documentation, as well as TPP T.AMC.POWR.96.0008 for a more complete Test and Acceptance
NOTE: When testing alarms and functions, be sure not to interrupt service
Comments (all No answers must be commented on — Please use the back of this form for additional comments)

## Form 826C Fuel Tst Chklst
Form 826C
FUEL TANK, FUEL SYSTEM, AND FUEL MONITOR
TEST & ACCEPTANCE CHECKLIST
Site: | 0 | BVAPP: | 0
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM |  |  | YES | NO
1. Fuel in main and day tanks is sufficient and free of excess water and other contaminants
2. Ensure that outdoor tanks are placed in such a position that water will not flow into or pool on top of them.
3. If the outdoor Diesel fuel tank is aboveground in a climate where temperatures may get below 32˚ F, ensure that the tank is either using #1 Diesel fuel, or is equipped with a tank heater.
4. Visually ensure that all fuel tanks (both main and day) have containment that will contain all of the fuel in the tank in case of a leak.
5. Inspect tank(s) and all fuel piping and pumps for any leaks
6.Ensure fuel lines are connected to engine through a flexible section
7. Fuel Lines are installed and routed in accordance with the vendor-supplied Engineering specs and drawings.
8. Verify that an anti-siphon valve is installed on the fuel suction line at the first entrance point to the generator room. The melt link should be 195 degrees.
9. Verify that an electric fuel solenoid (operating from the engine start and/or control batteries at 12 V or 24 VDC) is installed on the supply line at each generator’s fuel pump’s flex hoses. The solenoid must be connected to the generator run circuit in the control panel.
10. Verify that fuel lines running on the floor are routed so as not to create a safety hazard. (Fuel lines lying on the floor should be covered with a metal shroud, and the shroud should be painted yellow or yellow with black diagonal stripes.)
11. Verify that the fuel lines are Aero-quip or Strotoflex hose or black iron. (Aero-quip and Stratoflex lines are permitted, but must be run inside a containment conduit. Galvanized pipes and fittings are not permitted.)
12. Verify that the fuel return line is free from all obstructions. (No gates, valves, or traps are permitted.)
13. Ensure proper operation of all fuel pumps, plus any day tank valves
14. Ensure that a low fuel alarm is reported as a minimum (may be reported as a generic fuel system trouble) all the way to the NROC Center. The low fuel alarm should report when there is 8 hours or more of fuel left.
15. If site is equipped with a fuel tank monitor, ensure that it has at least a generic fuel system trouble alarm wired and reporting all the way to the NROC Center
16. Ensure fuel tank monitor is equipped with a dialup modem and a working phone line (some radio sites and other sites where phone service is inaccessible may be exempt from this requirement), and that Power NROC and the local Power Crew have that number.
17. Ensure that the fuel tank monitor is equipped with paper tape and ink, and a method of storing the paper tape.
18. Ensure that all fuel lines and tanks are properly grounded in accordance with Qwest Tech Pub 77355.
NOTE: Use supplier documentation, as well as TPP T.AMC.POWR.96.0008 for a more complete Test and Acceptance
NOTE: When testing alarms and functions, be sure not to interrupt service
Comments (all No answers must be commented on — Please use the back of this form for comments)

## Form 827 OSP Tst Chklst
Form 827
OUTSIDE PLANT SITE TEST & ACCEPTANCE CHECKLIST
Site: | 0 | BVAPP: | 0
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM |  |  | YES | NO
1. Ensure that internal and external grounding is per Qwest Technical Publication 77355. Ensure proper grounding of the site using a megger.
2. Do ventilation and exhaust openings have free access
3. Ensure that the site and all of the bays and wiring in the RT are properly tagged/stenciled
4. Ensure proper operation of A/C, sump pump, gas monitor and other environmental systems with the vendor present for CEVs, CECs, and huts, as applicable
5. Ensure safety equipment (e.g., fire extinguisher, first aid kit, gloves, eyewash fluid, etc.) is present, as applicable
6. Ensure that all holes in a CEV are properly sealed
7. Emergency lighting, gas monitors, environmental controllers, or any other device that should be powered by -48 VDC is connected to the DC Plant.
8. Site properly constructed, landscaped, and backfilled; and weeds are abated
9. Emergency engine connection available and sized properly. Verify that a generator can be parked within 10 ft of the transfer switch, and that the soil is such that there is access under adverse weather conditions. After turn-up, transfer the site to generator to confirm backup.
10. Site has records/forms for proactive maintenance of the power plant. Ensure that the power plant was turned up correctly per Forms 823A and B. Load tests the plant and batteries.
11. Ensure continuity of power and environmental alarms, and any other alarms to the NROC Center (Power Major, Power Minor, Intrusion, High Temperature, and Explosive Gas Alarm for CEV/Cs are a minimum). If a mux is used, verify that it is configured for phase 2 and provisioned for X.25/TL1. (See Standard Configuration and REGN 154-103-001 for power and environmental alarm standards.)
12. Lightning/surge arrestor installed in power pedestal, and power pedestal wired per the NEC
13. Confirm that controlled environment sites are set to operate within 55-85° F.
This Test & Acceptance checklist should be performed with the installer(s)/contractor(s) on site. Note on attachment all problems they fix
Comment below or attach comments (all No answers must be commented on)

## Form 828A CO Grnd Tst Cklst
Form 828A
CO GROUNDING TEST & ACCEPTANCE CHECKLIST
Site: | 0 | BVAPP: | 0
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM |  |  | YES | NO
1.The site ground is the proper size, and installed in accordance with the site record drawings, Engineering instructions, and Qwest Technical Publication 77355
2. Both ends of all site ground cables are tagged, and designated to show opposite end terminating location
3. All site ground cables between floors and through wall are run through nonmetallic sleeves or conduit. If site ground leads are run through metallic conduit or sleeves, both ends of the conduit or sleeve are bonded to the site ground lead.
4. Isolated frames, cabinets, rectifiers, etc. containing AC service are properly grounded (usually identified with green-wire ground)
5. If associated switching system uses isolated grounding, integrity must meet the system requirements spelled out in Qwest Technical Publication 77355
Test & Acceptance should be performed with the installer on site. Note below all problems they fix
For a complete grounding review, contact the NROC Center
Comments (all No answers must be commented on)

## Form 828B Pwr Bar & Cable cklst
Form 828B
POWER DISTRIBUTION BUS BAR & CABLING
TEST & ACCEPTANCE CHECKLIST
Site: | 0 | BVAPP: | 0
Associated Power Plant |  | Location
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM |  |  | YES | NO
1. AC bus duct and conduit is installed in accordance with site record drawing layout, and the manufacturers' specifications
2. The proper type and size fuses and/or circuit breakers are installed in AC bus duct plug-in units
3. Warning labels are placed at all access openings and end sections of AC bus duct, as required
4. Bus bar is installed in accordance with site record drawing layout
5. Bus bars and risers are stenciled to properly identify CHARGE, DISCHARGE, BAT, GRD, voltage, etc.
6. The ammeter shunt is properly mounted and stamped to indicate voltage and ampere rating
7. Installation meets Qwest workmanship standards, and is in accordance with Engineering standards and drawings, as spelled out in Qwest Technical Publications 77350, 77351, 77352, 77355 and 77385
8. Bus bars, joints, and terminating connections to bus bars are free of excessive heat. (Technicians may use heat strips, or heat guns to determine heating. If major problems are suspected, a Power NROC Tech Support person may be called in to do a scan with a thermal camera)
9. Power cable is routed in accordance with site record drawings
10. Power cable is run and secured on cable racks
11. Adequate insulating protection is provided on cable rack straps, stringers, thread rods, auxiliary frame bars, and other metallic objects where power cable makes contact with sharp surfaces
12. Power cable insulation is free of damage
13. Terminating wires and cables are properly tagged and designated at both ends of conductors when required
14. All cables listed on power cable running list are installed with correct type and size of cable as specified, or otherwise calculated
Test & Acceptance should be performed with the installer on site. Note below all problems they fix
Comments (all No answers must be commented on)

## Form 829A Pwr Flr Plan Cklst
Form 829A
POWER AREA FLOOR PLAN TEST & ACCEPTANCE CHECKLIST
Site: | 0 | BVAPP: | 0
Associated Power Plant |  | Location
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM |  |  | YES | NO
1. Power equipment is located and designated as shown on floor plan drawing
2. All cable holes appear to be closed properly (wall, ceiling, and floor type, as applicable)
3. Wall and column mounted equipment are properly located and shown on floor plan, cable rack plan, or other associated site record drawings
Test & Acceptance should be performed with the installer on site. Note below all problems they fix
Comments (all No answers must be commented on)

## Form 829B Pwr Tst Chklst
Form 829B
POWER DOCUMENTATION TEST & ACCEPTANCE CHECKLIST
Site: | 0 | BVAPP: | 0
Associated Power Plant |  | Location
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM |  |  | YES | NO
1. All new power equipment drawings furnished on this project are in acceptable condition
2. All power drawings that were supposed to be provided with this job were provided
3. All operating and maintenance instructions for new or added power equipment are available and accessible at the site
4. All installer job completion reports are available
5. Installer(s) followed written MOPs
Test & Acceptance should be performed with the installer on site. Note below all problems they fix
Comments (all No answers must be commented on)

## Form 840 CO Pwr Equip Inv
0
Form 840
0
CENTRAL OFFICE POWER EQUIPMENT INVENTORY
OFFICE: | 0 | CLLI: | 0 | DATE:
ADDRESS: | 0 | TECH: |  | PHONE:
BATTERY PLANTS
| Plant #1 | Plant #2 |  | Plant #3
Voltage & Polarity:
Plant/Controller Mfr. & Model:
Plant Size (shunt & bus bar ampacities):
Rectifier Fr & Model:
Battery Strings & A-hr Size:
Battery Fr & Model:
Battery Installation Date:
Plant Load in Amps:
PDSC Bus Ampacity & Fdr Fuse/Brkr Size:
add Rect. max loads for total max on PDSC:
CONVERTER PLANTS
| Plant #1 | Plant #2 |  | Plant #3
Voltage & Polarity:
Fr & Model:
Associated Battery Plant:
Qty & Sizes of Converters:
Plant Load in Amps:
RING PLANT(S) |  | PSMC MONITOR and OTHER ALARM DEVICES
Fr: | Model: | PSMC Fr & Model:
Ringers: | Interrupters: | Software Version:
Tone Generators: | Installation Date: | Dial-Up #:
INVERTER(S)/UPS |  | X.25 Ckt #:
Fr & Model: |  | Other Alarm Devices (e.g., Dantel, etc.):
Size, AC Voltage/Phase: |  | ENGINE & TANK DATA
Load (AC Amp/kVA): |  | Fr & Model:
Associated Battery Plant: |  | Voltage & kW:
Installation Date: |  | Install Date (note if not Autostart):
COMMERCIAL AC |  | Fuel Type & Consumption (gal/hr):
Voltage & Phase: |  | Actual Engine Load (in kW):
Size (Amps): |  | Alitiude
Lightning Arrest Fr & Model: |  | Start Batt Fr & Model:
PORTABLE GENSET INFORMATION |  | Start Batt Install Date:
Plug Fr, Mod, & Size (Amps): |  | Xfr Switch Type/Size:
Portable Fr, Size, Fuel: |  | Day Tank Capacity (gal):
Storage Location: |  | Main Tank Type & Capacity (gal):
Tank Monitor Fr & Model:
NOTES & COMMENTS (use back of sheet as needed) |  | Tank Monitor Dialup:
Retain a copy of this form and send a copy to the Power Engineers (http://saw3/NROC/Power/power-mop/Directory.html)

## Form 841 BDFB-PBD Assign Rec
0
Form 841
0
BDFB OR POWER BOARD PANEL FUSE/BREAKER ASSIGNMENT RECORD
Site: | 0 | CLLI: | 0 |  | Date:
Address: | 0
Tech: |  |  |  | Phone/Pager:
PBD/RR of this BDFB/PBD: |  |  |  |  | PANEL(s):
Fdr Fuse/Brkr PBD & Position: |  |  | Fdr Fuse/Brkr Size: |  |  | Panel Load:
Position # | Equipment & Relay Rack Fed |  |  | Fuse or Brkr Size | Mfg L-2 Drain | Mfg L-1 Drain | Actual Load
Totals
additional panels may be placed on additional sheets
List 2 drains are peak drains (fuses sized at 125% minimum of this; and cable sized from them too), and List 1 drains are average drains
assigning fuses from the bottom to the top of a bay or panel (or inside to outside for horizontal panels)
eases future installation and reduces cable congestion
as needed, contact your Design Engineer for a fuse assignment (if those are tracked in your area)
Please note if this Panel is "bussed" or "cabled" in the rear to adjacent panels (e.g., C, A2, etc.)
information for all columns may not be available to you — some columns are for Engineering use, and some for the "field"
Notes:

## Form 844 Critical Pwr Alm cklst
0
Form 844
0
CRITICAL CO POWER AND ENVIRONMENTAL ALARM VERIFICATION
Alarm |  | NMA tkt # | Notes
Critical Power Alarms
Commercial AC Fail
Power Major
Power Distribution Fuse/Breaker Major
Low Voltage and/or Battery on Discharge
Very Low Voltage (if applicable)
High Voltage
Rectifier Fail Major
Ring Plant Major
Low Voltage Disconnect (where applicable)
Engine Run
Engine Fail/Major
Critical Environmental Alarms
High Temperature (of the site or any room therein)
Fire Alarm
Fire System Trouble
High Water/Sump (in cable vault, if applicable)
Open Door/Intrusion
Alarm Center Contact Person: |  |  | Alarm Center Phone:
Site CLLI: | 0 | Site Address: | 0
Alarm Telemetry System Type:
X.25 (PSMC) | e-tel (Dantel, E2A, Westronics) |  | Switch or other
NROC Tech with whom Test performed: |  |  | Phone:
It may not be wise to test some alarms except in the Maintenance Window due to the possibility to cause an outage if they are truly tested; and/or in some cases, it may be best to simply verify alarm continuity by shorting the alarm pins instead of actually bringing in the alarm, for the same reasons
Environmental Alarms may be tested by Real Estate
Additional Notes:

## From 845 OSP Equip Inv
0
Form 845
0
OUTSIDE PLANT POWER EQUIPMENT INVENTORY
Common Name of Location | 0
State | 0
CLLI | 0
Address | 0
Upstream Office (serving Wire Center)
Access & Directions
Map coordinates (if applicable)
Customer (primarily for Customer Prem sites)
Site Type (RT, CEV, UE, CEC, hut, rptr, CPE)
(list RTs by type: e.g., 80 cabinet, etc.)
Date of this review
Reviewer name & contact #
Air-conditioning type & maintenance contact
Power plant type (also list J-spec, KS-, or model #)
Load (in Amps)
# Rectifiers
Rectifier type [also list the model number(s)]
Rectifier size(s)
Float Voltage
# Battery strings
Battery type (model #, KS-spec, etc.)
Battery size (A-hrs)
# cells per string
Battery installation date(s)
Residual Ring plant type (model number, etc.)
Comm. AC voltage, phase, and Amp rating
Generator Plug Mfg., type, and size
Alarm system (E-tel, X.25, overhead, etc.)
Alarm Center & Center phone #
CIRCLE ALARMS THAT ARE PRESENT (Add any others not listed here)
POWER MJ POWER MN RECT. FAIL OPEN DOOR LOW TEMP HIGH TEMP
AC PWR FAIL SMOKE/FIRE HUMIDITY SUMP PUMP COMBUSTIBLE GAS TOXIC GAS
Notes:

## Form 846 Equip Enc Alm Ver
0
Form 846
0
OSP EQUIPMENT ENCLOSURE HOUSEKEEPING ALARM VERIFICATION
Alarm |  | Works? | Doesn’t Work? | N/A
Commercial AC Fail
Power Major
Power Minor
High Battery Temperature
Power Distribution Fuse/Breaker
Low Voltage and/or Battery on Discharge
Very Low Voltage
High Voltage
Rectifier Fail (list the number of these alarms if more than 1)
Ring Plant Major
Ring Plant Minor
High Temperature (of the enclosure)
Explosive Gas Alarm
Toxic Gas Alarm
Toxic/Explosive Gas Alarm (combined)
Fire Alarm
Fire System Trouble
High Water
Sump Pump Failure
Open Door/Intrusion
Ventilation/Fan Fail
Air-Conditioner Failure
High Humidity
Tech Performing Test: |  | Phone/Pager:
Site CLLI: | 0 | Site Address: | 0
Alarm Telemetry System Type:
X.25 overhead (fiber mux) | e-tel (Dantel, E2A, Westronics) |  | other (list)
NROC Tech with whom Test performed: |  |  | Phone:
Additional Notes: