Qwest

Technical Publication

Power Equipment and Engineering Standards

Copyright 1996 - 2009  	77385

Printed in U.S.A.	Issue I

All Rights Reserved	May 2009

NOTICE

All requirements in this document are effective from the publication date of the document forward.

This document should be used in conjunction with Qwest Technical Publications 77350, 77351, 77355, and 77354; Telcordia Recommendations; relevant Alliance for Telecommunications Industry (ATIS) documents; relevant American National Standards Institute (ANSI) documents; Institute of Electrical and Electronics Engineering (IEEE) standards; Federal Communications Commission (FCC) rules; the National Electrical Code (NFPA 70); Underwriters Laboratories Requirements; Department of Labor - Occupational Safety and Health Standards (OSHA 29 CFR, Part 1910); and Federal, State, and local requirements including, but not limited to, statutes, rules, regulations, and orders of ordinances imposed by law.  Detail engineering for Qwest sites shall meet all of the above references, as well as Qwest Standard Configuration Documents.

This document supersedes Module 1; Part C of Technical Publication 77351 (Power Engineering Standards section) issues prior to 1996.

QWEST Communications, Inc. reserves the right to revise this document for any reason, including but not limited to, conformity with standards promulgated by various governmental or regulatory agencies; utilization of advances in the state of the technical arts; or to reflect changes in the design of equipment, techniques, or procedures described or referred to herein.

Liability to anyone arising out of use or reliance upon any information set forth herein is expressly disclaimed, and no representation or warranties, expressed or implied, are made with respect to the accuracy or utility of any information set forth herein.

This document is not to be construed as a suggestion to any manufacturer to modify or change any of its products, nor does this publication represent any commitment by Qwest to purchase any specific products.  Further, conformance to this publication does not constitute a guarantee of a given supplier's equipment and/or its associated documentation.

Ordering information for Qwest Technical Publications can be obtained from the Reference Section of this document.

COMMENTS

PLEASE TEAR OUT AND SEND YOUR COMMENTS/SUGGESTIONS TO:

Qwest

Local Network Power Tech Support

700 W. Mineral Ave, MT-H22.13

Littleton, CO  80210

fax:  (303) 707-9041

E-mail: techpubs@qwest.com

Information from you helps us to improve our Publications.  Please take a few moments to answer the following questions and return to the above address.

Was this Publication valuable to you in determining

our requirements?	YES 		NO

Was the information accurate and up-to-date?	YES 		NO

Was the information easily understood?	YES 		NO

Were the contents logically sequenced?	YES 		NO

Were the printed pages legible?	YES 		NO

If you answered NO to any of the questions and/or if you have any other comments or suggestions, please explain:

(Attach additional sheet, if necessary)

Name 			Date

Company

Address

Telephone Number

Email	_______________________________________________________________________

CONTENTS

Chapter and Section 	Page

1.	General Requirements and Definitions	 1-1

1.1	General	 1-1

1.2	Reason For Reissue	 1-2

1.3	Requirement Applicability	 1-2

1.4	AC Requirements	 1-3

1.5	Generic Technical Requirements	 1-6

1.6	NEBS Requirements	 1-9

1.7	Generic Alarming Requirements	 1-10

2.	DC Power Plants and Rectifiers	 2-1

2.1	Overview	 2-1

2.2	General DC Power Plant Requirements	 2-1

2.3	Charging Equipment (Rectifiers)	 2-5

2.4	Engineering Guidelines	 2-8

2.5	Power Board Panel and Fuse Numbering for New Plants	 2-11

2.6	Conventional Controller	 2-12

3.	Batteries	 3-1

3.1	Overview	 3-1

3.2	General Description	 3-1

3.3	Battery Discharge Characteristics	 3-1

3.4	Battery Recharge Characteristics	 3-3

3.4.1	Ventilation of Battery Areas	 3-4

3.5	Battery Configurations	 3-5

3.6	Battery Types	 3-6

3.7	Selection	 3-10

3.8	Sizing	 3-10

3.9	Battery Stands and Connections	 3-11

3.9.1	Metal Stands, Trays, and Compartments/Boxes	 3-11

3.9.2	Round Cell Stands	 3-12

3.9.3	Battery “Stand” Installation	 3-13

3.10	Battery Disconnects	 3-18

4.	Converters	 4-1

4.1	General	 4-1

4.2	Alarm Features	 4-1

4.3	Technical Requirements	 4-1

CONTENTS (Continued)

Chapter and Section 	Page

5.	Inverters (DC/AC)	 5-1

5.1	General	 5-1

5.2	Inverter Selection	 5-2

5.3	Load Classification	 5-2

5.4	Alarm Features	 5-2

5.5	Technical Requirements DC and AC Power Supplies	 5-2

6.	Uninterruptible Power Supplies (UPS)	6-1

6.1 	General	6-1

6.2 	Definition of Terms	6-1

6.3 	Technical Requirements	6-3

6.4 	Alarming and Control	6-5

7.	Standby Engine-Alternators	7-1

7.1	General	7-1

7.2	Site AC Power Systems	7-3

7.3	Sizing and Ratings	7-4

7.4	Alternator Technical Requirements	7-5

7.5	Control Cabinet and Transfer System Requirements	7-6

7.6	Additional Engine Requirements	7-12

7.7	Voltage and Frequency Regulation	7-12

7.8	Additional Paralleling Requirements	7-14

7.9	Alarms and Shutdowns	7-15

7.10	Fuel and Lubrication Systems	7-18

7.11	Exhaust System Requirements	7-22

7.12	Starting Systems	7-23

7.13	Cold Starting Aids	7-23

7.14	Acoustic Noise	7-24

7.15	Cooling System	7-25

7.16	Safety	7-26

7.17	Hazardous Voltages	7-27

7.18	Portable Engines and Trailers	7-27

7.19	Portable Engine Connections	7-28

CONTENTS (Continued)

Chapter and Section 	Page

8.	Power System Monitor/Controller (PSMC)	8-1

8.1 	General	8-1

8.2 	Standard Monitor and Control Points	8-2

8.2.1	Primary Power Plant	 8-2

8.2.2	Rectifiers	 8-3

8.2.3	Batteries	 8-3

8.2.4	Converter Plants	 8-4

8.2.5	Inverters	 8-4

8.2.6	Ringing Plants — Toll Ringing Plants for Non-Switched        Circuits	 8-5

8.2.7	Uninterruptible Power Supplies (UPS)	 8-5

8.2.8	Standby Engines and Transfer Systems	 8-5

8.2.9	AC Power	 8-7

8.3 	Alarms	8-7

8.4 	Statistical Channels	8-7

8.5 	Energy Management and Sequencing	8-8

8.6 	Requirements of a PSMC for Confined Locations	8-8

8.6.1	Primary Power Plant	 8-9

8.6.2	Rectifiers	 8-9

8.6.3	Batteries	 8-9

8.7 	Power Alarms in Sites Without a PSMC	8-10

9.	DC Power Distribution	9-1

9.1	General	9-1

9.2	Telecommunications Equipment Loads	9-1

9.3	Power Plant Distribution Characteristics	9-6

9.4	Cabling and Bus Bar	9-7

9.5	Protectors and Cable Sizing	9-11

9.6	Fuse Sources	9-13

9.7	Bus Bar Labeling and Layouts	9-23

CONTENTS (Continued)

Chapter and Section 	Page

10.	Ring, Tone and Cadence Plants	10-1

10.1	General	10-1

10.2	Ringing and Tone Systems Technical Requirements	10-1

10.3	Distribution	10-2

10.4	Ringing Plant Alarms and Troubles	10-2

11.	Power Pedestals	 11-1

11.1	General	 11-1

11.2	Materials	 11-1

11.3	Technical Requirements	 11-2

12.	Lighting	 12-1

12.1	Emergency	 12-1

12.2	Task	 12-1

13.	Standard TL1 Messages and Alarm Settings for Power	 13-1

13.1	General	 13-1

13.2	AIDs and Condition Types for Power Alarms	 13-2

13.3	“Reduced Character” and Overhead Bitstream TL1 Condition             Types	 13-7

13.4	TL1 Query Messages for Power	 13-9

13.5	Analog Power Alarm Set Points (Thresholds)	 13-11

13.6	Typical Power Alarm and Monitor Points	 13-20

13.6.1	Typical PSMC-CL Points in Smaller Sites	13-21

13.6.2	Typical Central Office Power Alarm Points	13-23

13.7	Power SNMP Traps for DSL and Ethernet Locations	 13-26

CONTENTS (Continued)

Chapter and Section 	Page

14.	Power Audits	 14-1

14.1	Scope	 14-1

14.2	Power Plant Audit	 14-1

14.3	Check List	 14-1

14.3.1	Power Plants	 8-2

14.3.2	Batteries	 8-3

14.3.3	What Cable Racking is Required?	 8-3

14.3.4	How Much Cable is Piled on the Cable Rack and is any Blocked?	 8-3

14.3.5	Floor Loading of Equipment	 8-3

14.3.6	Converter Plants	 8-4

14.3.7	Ringing Plants	 8-4

14.3.8	AC Equipment	 8-4

14.3.9	Standby Engine Alternator	 8-4

14.3.10	Lighting	 8-5

14.3.11	Battery Distribution Fuse Boards (BDFBs)	 8-5

15.	Turn Up, Test, and Acceptance Procedures	 15-1

15.1	General	 15-1

15.2	Maintenance Window Guidelines for Power	 15-1

16.	Definitions and Acronyms	 16-1

17.	References	 17-1

17.1	Telcordia Publications	 17-1

17.2	Qwest Technical Publications	 17-2

17.3	Miscellaneous Publications	 17-2

17.4	Ordering Information	 17-5

CONTENTS (Continued)

Tables	Page

1-1	Operating Voltage Ranges for AC-Powered Equipment	1-4

1-2	Color Codes for AC Wire	1-4

1-3	Summary of Minimum Lab Testing Requirements for DC Power           Equipment	1-10

1-4	Color Codes for Equipment Visual Indicating Lights	1-11

3-1	Typical Battery Disconnect Sizes for Flooded Cells	3-19

12-1	Wire and Protector Sizing for -48 VDC Powered Lighting Circuits	12-3

13-1	AID for Power Alarms	13-3

13-2	Power Alarm Condition Types	13-5

13-3	“Reduced Character” and Overhead Bitstream TL1 Alarm Condition                        Types	13-8

13-4	TL1 Query Messages for Power	13-9

13-5	Part 1A:  Alarm Thresholds on Analog Points — DC Voltage for Flooded Lead-Acid Battery Plants	13-12

13-5	Part 1B:  Alarm Thresholds on Analog Points — DC Voltage for typical VRLA Battery Plants	13-14

13-5	Part 1C:  Alarm Thresholds on Analog Points — DC Voltage for “Constant Current” Charging Applications of VRLA Batteries	13-14

13-5	Part 1D:  Alarm Thresholds on Analog Points — DC Voltage Set Points for Lithium-based Batteries	13-14

13-5	Part 1E:  Alarm Thresholds on Analog Points — DC Voltage Set Points for Converter Plants and Engine Start Batteries	13-15

13-5	Part 2:  Alarm Thresholds on Analog Points — Temperature Compensation and Current Limiting	13-16

13-5	Part 3:  Alarm Thresholds on Analog Points — Temperatures	13-17

13-5	Part 4:  Alarm Thresholds on Analog Points — DC Current	13-18

13-5	Part 5:  Alarm Thresholds on Analog Points — AC Voltage	13-19

13-5	Part 6:  Alarm Thresholds on Analog Points — AC Current	13-20

13-5	Part 7:  Alarm Thresholds on Analog Points — Fuel Alarm Thresholds	13-20

13-6	Part 1A:  Typical Power Alarm and Monitoring Points for OSP Cabinets and Customer Premise	13-21

13-6	Part 1B:  Typical Power Alarm and Monitoring Points for CEVs, huts, CdOs (small COs without an engine) and Radio Sites (PSMC-CL or             PSMC)	13-22

13-6	Part 2:  Typical Power Alarm and Monitoring Points for Central Offices with Engines	13-24

CONTENTS (Continued)

Tables	Page

13-7	SNMP Power Alarm Messages used in Qwest	13-26

14-1	BDFB Capacity Table	14-6

Figures	Page

2-1	A Powering Scheme for a Central Office	2-1

2-2	Typical Outside Plant Equipment Enclosure Power Scheme	2-2

2-3	Typical Radio Site Power Scheme	2-2

3-1	Typical Arrangement of Cables for a Battery Stand	3-16

3-2	Minimum Dimensions for a Bus Bar above Battery Stands	3-17

7-1	30-Ampere Cable Hardwired to Single-Phase Engine-Alternator	7-33

7-2	30-Ampere Cable to Single-Phase Engine-Alternator Receptacle	7-33

7-3	100-Ampere Cable Hardwired to Single-Phase Engine-Alternator	7-34

7-4	100-Ampere Cable to Single-Phase Engine-Alternator Receptacle	7-34

7-5	100-Ampere Cable Hardwired to Three-Phase or Single/Three-Phase Engine-Alternator	7-35

7-6	100-Ampere Cable to Three-Phase or Single/Three-Phase Engine-Alternator Receptacle	7-35

7-7	200-Ampere Cable Hardwired to Single-Phase Engine-Alternator	7-36

7-8	200-Ampere Cable to Single-Phase Engine-Alternator Receptacle	7-36

7-9	200-Ampere Cable Hardwired to Three-Phase or Single/Three-Phase Engine-Alternator	7-37

7-10	200-Ampere Cable to Three-Phase or Single/Three-Phase Engine-Alternator Receptacle	7-37

CONTENTS (Continued)

Figures (Continued)	Page

9-1	Switch Distribution Voltage Drops Loops	9-4

9-2	Equipment Distribution Voltage Drops Loop	9-5

9-3	Voltage Drops from Battery Strings to PBDs	9-5

9-4	Typical Mounting of a Bus Bar above PDFs and Battery Stands	9-11

9-5	BDFB Fuse Assignment Label	9-16

9-6	Typical Layout of BDFB Fuse Panels	9-17

9-7	Typical Layout of 2 Load 600 Ampere BDFB	9-18

9-8	Typical Layout of 4 Load 400 Ampere BDFB	9-19

9-9	Typical Return Bus Bar Mounting for a 7’ BDFB (View A-A)	9-20

9-10	Typical Return Bus Bars Mounting for a 7’ BDFB (View B-B)	9-21

9-11	Load and Embargo Labels for BDFBs	9-22

9-12	Example of Bus Bars (Term Bars) above a Battery Stand	9-23

9-13	A Battery Return Bus Bar above a BDFB	9-24

9-14	Chandelier Hot Side Main Terminal (Term) Bar	9-24

9-15	Chandelier Return Side Bar	9-24

9-16	Example of a Remote Ground Window	9-25

9-17	Example Main Return / Ground Window MGB Bar	9-25

9-18	Example of Sandwiched Terminations	9-26

CONTENTS (Continued)

Forms	Page

820	Generic Test and Acceptance Checklist	15-4

821A	Power Room Lighting Test and Acceptance Checklist	15-5

821B	Alarm and/or Power Monitor/Controller (PSMC) Test and  Acceptance Checklist	15-6

821C	BDFB, Power Board, or Fuse Panel Test and Acceptance Checklist	15-7

822	Batteries and Stands Test and Acceptance Checklist	15-8

823A	Rectifier Test and Acceptance Checklist	15-9

823B	Power/Battery Plant Test and Acceptance Checklist	15-10

824A	Converter Plant Test and Acceptance Checklist	15-11

824B	Residual Ring Plant Test and Acceptance Checklist	15-12

825A	Inverter Test and Acceptance Checklist	15-13

825B	UPS Test and Acceptance Checklist	15-14

826A	Standby Engine Test and Acceptance Checklist	15-15

826B	Transfer System and AC Service Entrance Test and Acceptance Checklist	15-16

826C	Fuel Tank, Fuel System, and Fuel Monitor Test and Acceptance Checklist	15-17

827	Outside Plant Site Test and Acceptance Checklist	15-18

828A	CO Grounding Test and Acceptance Checklist	15-19

828B	Power Distribution Bus Bar Test and Acceptance Checklist	15-20

829A	Power Area Floor Plan Test and Acceptance Checklist	15-21

829B	Power Documentation Test and Acceptance Checklist	15-22

840	Power Equipment Inventory	15-23

841	BDFB/PBD Panel Fuse/Breaker Assignment Record	15-24

844	Critical CO Power Alarm Verification	15-25

845	Outside Plant Power Equipment Inventory	15-26

846	Outside Plant Equipment Enclosure Housekeeping Alarm Verification	15-27

CONTENTS

Chapter and Section 	Page

1.	General Requirements and Definitions	 1-1

1.1	General	 1-1

1.2	Reason For Reissue	 1-2

1.3	Requirement Applicability	 1-2

1.4	AC Requirements	 1-3

1.5	Generic Technical Requirements	 1-6

1.6	NEBS Requirements	 1-9

1.7	Generic Alarming Requirements	 1-10

Tables

1-1	Operating Voltage Ranges for AC-Powered Equipment	1-4

1-2	Color Codes for AC Wire	1-4

1-3	Summary of Minimum Lab Testing Requirements for DC Power           Equipment	1-10

1-4	Color Codes for Equipment Visual Indicating Lights	1-11

# 1.	General Requirements

## 1.1	General

This section is intended to provide general requirements that apply to all of the units of the document, which follow.

All power equipment shall be Manufactured, Engineered, and Installed in accordance with the following:

- Qwest Technical Publications

    - Detail engineering for Qwest sites shall meet all the standards stated herein;

    - Qwest standard configuration documents; and

    - Qwest fire and life safety practices.

- Telcordia Recommendations

- Alliance for Telecommunications Industry (ATIS) documents

- American National Standards Institute (ANSI) standards

- Institute of Electrical and Electronics Engineers (IEEE) standards

- Federal Communications Commission (FCC) documents

- National Electrical Code (NFPA 70)

- Underwriters Laboratories (UL) Requirements

- Department of Labor - Occupational Safety and Health (OSHA) Standards

- Federal, State, and local requirements including, but not limited to, statutes, rules, regulations, and orders of ordinances imposed by law.

All power equipment used shall have passed through the Qwest Product Selection procedure.

All requirements in this document are effective from the date when they first appeared.

Qwest prefers that all end equipment carrying Network traffic be powered by nominal -48 VDC power (the equipment shall be capable of accepting Voltages at least from -42.75 to -56 VDC).  The primary power plant is typically a -48 VDC plant, although in some microwave radio sites, the primary plant may be -24 VDC.

While some modern equipment does use the -48 VDC directly, much of the equipment needs to convert it to other nominal DC Voltage levels, such as 3.3, 5, 9, 12, 24, 130, or 190 V.  This is usually done on a power supply card in the shelf with on-board “brick” chip DC-DC converters.  However, there are sometimes needs for bulk feeds to equipment at +24 V, -24 V, -130 V, or ±130 VDC.  In these cases, a large battery plant at the appropriate Voltage can be used, or a bulk DC-DC converter plant (see Chapter 4 for converter plant requirements) can be placed and powered from the primary -48 or -24 VDC plant.

If there is equipment carrying Network traffic that needs an uninterruptible AC source, it most preferably would use a feed from an inverter plant (see Chapter 5 for requirements for inverter plants).  In the case of very large uninterruptible AC needs, or Customer Premises installations (see Technical Publication 77368), a commercial UPS may be used (see Chapter 6 for requirements for UPS systems).  (For further information on AC requirements, see Section 1.3.)

The use of a blowtorch, acetylene torch, fiber fusion splicing equipment, or any open flames and/or sparks are not permitted in any Qwest battery room, per Qwest’s safety standards and the Fire Codes.

## Reason For Reissue

This document is being reissued to merge power standards for both the local and national sides of Qwest.  The changes impact internal Engineering and Intallation practices (as well as companies subcontracted by Qwest to do that work).  These changes will have little to minor impact on Competitive Local Exchange Carriers (CLECs).

## Requirement Applicability

Not all requirements in this document carry the same weight.  As a general rule the following applies:

| SHALL | When this designation is used in a requirement, it denotes a binding requirement (not optional) due to fire, life, or safety reasons. |
| --- | --- |
| MUST | When this designation is used in a requirement, it denotes a binding requirement, but does not involve fire, life, or safety. |
| WILL or SHOULD | When this designation is used in a requirement, it denotes a condition that is a Qwest preference. |

## AC Requirements

There are three types of AC loads that may be required within a Qwest telecommunication site.

- Protected Loads — protected loads will use either an inverter (Chapters 5) or UPS (Chapter 6).  If the inverter is operated in DC-preferred mode, or the UPS is “on-line” (aka double-conversion), there is no switching time (the power supplied is truly uninterruptible).  If the inverter is operated in AC-preferred mode, or the UPS is line-interactive, the static transfer switch in the inverter/UPS will switch to backup power during a power “event” in less than 4 milliseconds.

- Essential Loads — those telecommunications and building AC loads that must operate during prolonged loss of commercial AC power.  These loads are normally run off an on-site, auto-start, auto-transfer standby engine-alternator (Chapter 7).  An example of an essential load is air-conditioning in a larger building in a hotter climate

- Nonessential Loads — those that can experience long periods of commercial power interruption without needing some form of backup.  Generally, these loads are not switch-able to the standby source.  Most building lighting qualifies as non-essential loads, for example.  In smaller buildings, it may not be economical to provide two separate essential and non-essential busses.  In those, buildings, if they are equipped with an on-site engine, generally all the loads are on the essential bus.

All installed AC equipment will be provided with adequate working space as defined in the National Electrical Code (NFPA 70), Article 110.26.

AC equipment shall be capable of operating without damage from any input source with the following characteristics:

- The equipment shall be operational from a 60-Hertz (Hz) source (10%.

- •	Voltage Limits — The limits shown in Table 1-1 are consistent with range B utilization limits of American National Standard Institute (ANSI) Voltage Rating for Electrical Power Systems and Equipment, and apply to sustained Voltage levels:

Table 1-1 Operating Voltage Ranges for AC-Powered Equipment

| Phases | Nominal Voltage | Voltage Limits |
| --- | --- | --- |
|  |  | minimum | maximum |
| 1 | 120 | 106 | 127 |
| 1 | 220/240 | 184 | 254 |
| 1/3 | 208/240 | 184 | 254 |
| 3 | 277/480 | 424 | 508 |

AC circuits shall use THHN or THWN type wire, color-coded in red, blue, black, white, yellow, brown, orange, and green per Table 1-2.  THHN and THWN should not be used for DC applications except where they are run in conduit or within a bay where they are protected from abrasion or coldflow at impingement points.  The use of colored tape on both ends of the wire is acceptable for AC wire color coding, except that 6 AWG or smaller neutral conductors require a continuous white or natural gray outer finish along their entire length.  All AC wire approved for central office applications shall be run in conduit, raceway, or metallic enclosure.  Wire applications are defined in Chapter 9.

Table 1-2 Color Codes for AC Wire

| Nominal Voltage | Phase/Line/Leg | Color |
| --- | --- | --- |
| 240/120 | 1 | Black |
| 208/120 Y | A |  |
| 240/120 Δ |  |  |
| 240/120 | 2 | Red |
| 208/120 Y | B |  |
| 240 Δ |  |  |
| 208/120 Y | C | Blue |
| 240/120 Δ |  |  |
| 240/208 Δ | B | Orange |
| 480/277 Y |  |  |
| 480/277 Y | A | Brown |
| 480/277 Y | C | Yellow |
| Grounding | Green or |
|  | Green w/yellow stripe |
|  | or bare Copper |
| Neutral | White |
|  | or Gray |

All AC neutrals shall be sized at the same size as the phase conductors, at a minimum.

AC wires used in Outside Plant applications do not have to be run in raceway or conduit if they are cords terminated in a NEMA Twist-Lock plug.  These wires must be fire retardant Hypalon coated or polyethylene (XLP-USE-2, or EPR-USE-2, or RHH/RHW-2).

AC power wire shall be copper conductor only within the CO.  The AC feeds from the house service panel (HSP) to the Power Distributing Service Cabinets (PDSCs) serving the rectifiers shall be dual feed for DC plants rated 2400 Amps and larger and/or where the AC service entrance size is 500 A or larger.  One dual feed PDSC or two separately fed PDSCs will meet this requirement (if the separately fed PDSCs are served through step-up or step-down transformers, there should be one transformer for each PDSC).    Attempt to evenly split the rectifier loads among the PDSCs when there are multiple PDSCs.  PDSCs can be either stand-alone, wall mounted, or at the top of a rectifier bay.  The PDSC feeds from the house service board shall be sized to the capacity of that PDSC, (i.e., a 600-Ampere PDSC shall be sized and fed at 600 Amperes).  A PDSC shall be dedicated to that rectifier line-up which it is serving.  Circuit breakers for the rectifiers shall be sized to the manufacturers’ recommendation for the rectifiers being served.  PDSCs only need to be equipped with circuit breakers for existing rectifiers.  Future circuit breakers should be added when rectifiers are added to the power plant.  The cabinet and the circuit breakers will be rated for the available fault current (kAIC).  (The fault current available at that point may need to be calculated by a Professional [P.E.] Electrical Engineer.)  PDSCs for plants with an ultimate capacity of at least 2400 Amps DC should be rated at 600 Amps AC (and the feed to them should generally be at 600 Amps unless the entire site service entrance is not rated that high).  In smaller sites the PDSC can be rated as small as 100 Amperes, or some smaller sites may not even have a PDSC, but will have the rectifiers fed from the primary AC distribution panel directly.  OSP Sites that use a power pedestal for AC should be sized per Chapter 11.

All AC feeders in telecommunications equipment areas, (including power rooms), will be enclosed in conduit, or approved cable raceway.  Armored power cable (type AC, aka BX) or Liquid-Tite™ will only be used in special applications where rigid conduit is not practical and as specified by the NEC (see Chapter 9 of Technical Publication 77350 for rules governing the use of AC conduit types).  Flexible metal conduit shall not be used ever in power rooms per NEC Article 350.5(3), unless it is type MC.

All rigid, Electrical Metallic Tubing (EMT) and metallic liquid tight flexible conduit runs shall be made with steel compression or steel threaded type fittings, steel couplings, and junction boxes, unless they are larger than 1¼” diameter; in which case, set screw fittings are allowed, but not preferred.

No PVC conduit or tubing shall be used of any kind indoors or exposed outdoors.  It may be used for underground or concrete pour applications for AC service.

Horizontal runs of conduit across concrete pads in the OSP must be EMT or rigid metal.

AC feeds from the raceway or junction box to the rectifier/charger must be run in either thin wall or Liquid-Tite™ conduit.  Flexible conduit shall not be installed on cable racks.

Transient Voltage Surge Protection (TVSS) devices must meet and be Listed to UL 1449, second edition, the appropriate ANSI/IEEE C62 series document, and NEC articles 280 and/or 285 (it is also preferable that it be tested to NEMA LS 1).

The TVSS unit shall be as close as possible to the AC source (18 cable inches or less with no bends in the wire is preferred).  The TVSS shall be installed on the load side of the AC entrance unless it is also Listed and rated as a “Surge Arrestor”.  Installation must follow the manufacturers’ requirements.  If the TVSS is connected directly to the hot busses, it must have a minimum surge rating of 69 k.A.I.C.  If it is connected through breakers, the breakers should be a minimum of 30 Amps (preferably 60 Amps or larger).  Downstream TVSS are generally discouraged as unnecessarily costly unless they come as an integral part of the equipment (such as in a power strip or PDU), or are used to solve a specific proven problem.

For TVSS installed in COs or large Data Centers, the minimum kA suppression rating is 200 (400 or more preferred), with a minimum Joule rating of 5000.  These TVSS for larger installations should provide both common and transverse mode suppression.  For TVSS installed in OSP locations, the minimum kA suppression rating is 100 (200 or more preferred), with a minimum Joule rating of 2000 (3000 or more preferred).

## Generic Technical Requirements

All power equipment must conform to applicable American National Standards Institute (ANSI) requirements, and shall be Listed to the appropriate UL (Underwriters Laboratory) standard (if no other standard applies, UL1950/60950 probably does).  Power components (rectifiers/chargers, controllers/monitors, inverters, UPS, converters, engine-alternators, transfer systems, generator set plugs, AC power cabinets, and power pedestals) shall meet the applicable requirements of the National Electrical Code (NEC — NFPA 70), latest issue.

Powering equipment with non-metallic components must be fire-retardant rated as UL 94-V0 and have a minimum Limiting Oxygen Index (LOI) of 28% or greater.

All CO grounding cable (that is not manufacturer internal shelf and intra-bay wiring) shall be green in color, green with yellow stripe, or bare; and be in accordance with Qwest Technical Publication 77355.

All active electronic devices shall be solid-state.

All relays will be solid-state or provided with dust covers.

Protection devices can be either fuses or circuit breakers.  All protection devices shall be sized at a minimum of 125% of the peak load and rated for the available fault current (kAIC) which meets or exceeds the maximum available fault current at that point in the system.  All fuses or circuit breakers must be AC rated for AC circuits, and DC rated for DC circuits.  One spare fuse shall be provided for every 5 fuses ordered.

Fuses and breakers must be coordinated from a size and time-current curve perspective to increase the chances that the downstream protector is the first to blow/trip.

Fuses and circuit breakers shall be front accessible, and labeled to indicate their Ampere rating and circuit assignment (frame/shelf).  Circuit breaker size and trip setting should be visible without having to remove protective covers; or if the breaker size and trip setting is not visible, it should be posted on the protective cover.  Fuse size should be visible without having to open protective covers or remove power.  If this is not possible, the size of the fuse installed shall be posted on the outside of the cover where it is visible.  Circuit breakers shall be labeled according to the NEC.  When circuit breakers are mounted horizontally, the “UP” position shall be “ON”.  All circuit breakers should be equipped with shields to prevent accidental tripping.

Fuses must be color coded to prevent mixing.  Renewable link and H type fuses are not acceptable for use.  All internal circuits shall be protected with fuses mounted in a “dead front” fuse holder.  Internal fuses must be easily accessible.  Each fuse shall be provided with a blown fuse indicator connected to an alarm-indicating lamp on the control panel.  All power semiconductor circuits shall be fused using KAA type fuses to prevent cascading or sequential semiconductor failures.  All electrolytic capacitors shall be fused.  A maximum of two capacitors shall be protected by one fuse.

Parallel fusing (even with circuit breakers) is not allowed, per NEC Article 240.8.

If circuit breakers are used, they shall be of the thermal-magnetic type and trip free.  Contacts shall not be capable of being manually held closed during an overcurrent condition.

All power semiconductor circuits shall be fused to prevent cascading or semiconductor failures.

Insulating materials in arcing paths of contacts, fuses, etc. shall be of the non-tracking type.  Insulating material shall not be used that will independently support combustion, or that will ignite from a spark, flame, or heating.  The combustion products of insulating materials shall not combine with normal atmospheric air to form acid, toxic, or other deleterious products.

All DC runs under a raised floor or in a ceiling that is also used as an air plenum must be in a plenum rated raceway, metal conduit, or metallic liquid tight flexible conduit; or must be plenum-rated or MI or MC type cable.

For DC feeds in conduit, only two wires (one feed set — battery and return) can be ran in one conduit.  Each load (A, B, etc.) must be run in a separate conduit.

If forced air-cooling is used to keep power components cool the blower motors shall be equipped with sealed ball bearings, (this does not pertain to the HVAC system).  Blowers shall be redundant.  A failure of a blower unit shall generate an alarm.  All air inlet and exhaust openings shall be protected with expanded metal guards.

The structural members of power equipment shall not carry or conduct load currents.  Ferrous materials shall not be used for current carrying parts.

Metal parts, unless corrosion resistant shall have a corrosion protection finish.  Ferrous parts not required to meet an appearance criteria shall have zinc plate, cadmium plate, or an approved equivalent finish applied.  The minimum thickness of the finish shall be 0.0002 inches, plus a chromate treatment.  When dissimilar metals are used in intimate contact with each other, protection against electrolysis and corrosion shall be provided.  This protection may be metal plating or spraying, or use of a suitable insulating material (including a thin film of anti-oxidant if electrical conductivity needs to be maintained).

Nut, bolts, and screws should be grade 5 or equivalent for connection and mounting requirements.

Wire used for carrying load current shall be copper conductor only.  Wire subject to hinged action shall be of the stranded type.

Copper crimp-type connectors shall be used for all DC power wire connections.  Anti-galvanic corrosion joint compound shall be applied to connections.

Bus bar shall be of 95% hard-drawn copper.

All individual components of power equipment should be assigned a functional designation.  Each Test Point (TP) must be accessible and assigned a designation starting with TP1.  These designations shall be shown on the schematic drawing, on or adjacent to the point being designated.

Equipment that provides power (i.e. power plants, converters, inverters, BDFB, miscellaneous fuse panels, etc.) shall be designated as follows:

- Fuse or circuit breaker panels as panels;

- Rectifiers with a G and a numeric designation (G-01, etc.), and;

- Rectifier shelves as a shelf.

## 1.6	NEBS Requirements

NEBS will not be waived.

Qwest cannot and does not certify testing facilities.

The supplier shall meet the requirements of Telcordia GR-1089-CORE, and GR-63-CORE, as the GRs pertain to its equipment (pertinent requirements are determined by the third party test lab).  The supplier must test to the GRs as required by Qwest, and Telcordia SR-3580.  Qwest requires that all NEBS test be performed at an independent third party test facility.  These test facility must be accredited as part of a laboratory accreditation program sponsored by one of the following, American Association for Laboratory Accreditation (A2LA), National Voluntary Laboratory Accreditation Program (NVLAP), National Recognized Testing Laboratory (NRTL), and Underwriters Laboratories.  Test facilities must be certified for those fields of accreditation that encompass NEBS requirement.

Qwest will however accept test data from a supplier's testing facilities provided it is accredited to perform the test and observed by a member of another accredited laboratory as defined herein.  Qwest will not accept test reports written by the supplier or a supplier's interpretation of a test lab report.  Qwest will only accept test reports written by the independent test lab performing the work or by the representative of the observing third party lab.  All test reports must be written on the letterhead of the lab.

All components shall be tested as a system.  However, if individual components or subsystems have been tested a letter from the testing lab stating that the assembly of the unit or subsystems into the system will not change the NEBS data will be acceptable.

Note that wire and connectors used in the CO are not tested to NEBS, but do have to be Listed.  Equipment placed in non-Network areas (such as AC equipment or an engine in their own room) also do not have to be NEBS tested, but must be Listed.  Note also, that only equipment to be used in NEBS Earthquake Zones 3 and 4 must be tested to Zone 4 (equipment for use in COs in Zones 0-2 need only be tested to Earthquake Zone 2 criteria).

Table 1-3 Summary of Minimum Lab Testing Requirements for DC Power Equipment

| Requirement | Site Type |
| --- | --- |
|  | CO | CEV/C, UE, hut | RT Cab | Prem |
| Listed | X | X | X | X |
| NEBS 1 | X | X | X |  |
| Hardened |  | X | X |  |
| NEBS 2 | X |  |  |  |
| EMI NEBS 3 | X | X |  |  |
| ESD NEBS 3 | X | X |  |  |
| Earthquake | X |  |  |  |
| NEBS 3 | X |  |  |  |
| NEBS Other | X |  |  |  |

Note that the lab testing requirements listed in Table 1-3 apply to only a sample of the equipment (not every piece leaving the factory must be tested).  Note also, that these are the minimum requirements.  It would be desirable, for example, if Customer Premises and CEV DC power equipment that are to be placed in Earthquake Zone 3 or 4 were tested to those criteria, but it is not absolutely required.

## 1.7	Generic Alarming Requirements

All provided alarms will come equipped with a set of dry contacts so that the alarm can be remoted.  The connecting point for these contacts will be easily accessible.  All analog monitoring points (current shunts or Voltmeters) within the equipment will be equipped with terminal strip access (or screws that will accept ring terminals) for attaching remote monitoring devices.  The connecting point for analog monitoring points will be located near the alarm connecting points and be easily accessible.

All DC circuit breakers shall generate an alarm signal when in the tripped state (electrical or midtrip type breakers).  Battery disconnects shall also generate an alarm when turned off (mechanical trip).  For other breakers, whether to use breakers that generate an alarm in the off state (mechanical and electrical trip) is a decision left up to the Engineer.

The status indicators and alarm outputs shall be in the form of visual indicators in the plant (preferably lighted); and electrical signals for alarm sending circuits, and for connection to the office alarm system.  The visual alarm and status indication system shall have its own dedicated power supply circuit, operating from the plant Voltage.  This supply shall have an overcurrent protection device that will send a visual alarm when it has operated, or power has been removed from the "control and status" system.

Color-Codes for visual equipment indicators will be as follows:

Table 1-4 Color Codes for Equipment Visual Indicating Lights

| Color | Description |
| --- | --- |
| Green | Indicates proper operation of the system or equipment. |
| Amber, Orange, or Yellow | MINOR/PRELIMINARY — indicates an abnormal operating condition within the power system or equipment that requires attention, but power service to the load is not currently affected. |
| Red | MAJOR/CRITICAL indicates a failure that currently affects power service to the load, or a failure, which may mask an alarm, associated with a service-affecting problem. |
| White | Signify conditions that have none of the above connotations of red, yellow, or green. |

The alarm output for the office alarm system may have multiple outputs for each alarm (e.g., one for the local audible alarm system if it exists, one for the local visual alarm indications if they exist, and one for a remote alarm system).  If only one set of contacts exists for each alarm, they can be wired to all 3 systems (audible, visual, remote) if necessary (local audible and visual systems are used much less commonly now than they once were).  In some cases, the power equipment may have its own audible and visual alarm system.  The electronic or mechanical contacts for the alarms shall be capable of supporting 60 VDC and 0.5 Amperes, and shall be electrically isolated from each other and the frame ground.

It is desirable that an Alarm Cut-Off key or button (ACO) be provided to inhibit the office audible alarm function, without interfering with the visual or remote alarm systems.

A method shall be available to actively test all status indicators to verify they are in working condition.

Distribution fuse fail alarms for BDFBs and miscellaneous fuse panels in the IOF areas must be run to the local e-telemetry device (i.e., Dantel, E2A, etc.).  These alarm leads must be run in the switchboard cable rack.

Power alarm and monitoring leads that are within the power area only may be run on the side of the cable rack, on the horns, or on the hangers.  Waxed 9-cord shall be used for securing these leads.  Clips or wire ties are not acceptable for securing the alarm wires in this application in a Central Office.

Engine alarm leads (or other power alarm leads from non-traditional equipment areas without cable racking) may be run in conduit (inside the engine room, those leads must be run in conduit).

CONTENTS

Chapter and Section 	Page

2.	DC Power Plants and Rectifiers	 2-1

2.1	Overview	 2-1

2.2	General DC Power Plant Requirements	 2-1

2.3	Charging Equipment (Rectifiers) and their Controller	 2-5

2.4	Engineering Guidelines	 2-8

2.5	Power Board Panel and Fuse Numbering for New Plants	 2-11

2.6	Conventional Controller	 2-12

Figures

2-1	A Powering Scheme for a Central Office	2-1

2-2	Typical Outside Plant Equipment Enclosure Power Scheme	2-2

2-3	Typical Radio Site Power Scheme	2-2

# 2.	DC Power Plants, and Rectifiers

## 2.1	Overview

This unit covers requirements for DC power plants and rectifiers used within telecommunications facilities.

## 2.2	General DC Power Plant Requirements

One powering scheme for a Central Office is shown in Figure 2-1.  There are many other possible configurations.  A characteristic powering scheme for an Outside Plant equipment enclosure (e.g., CEV, cabinet, Customer Premise site, etc.) is shown in Figure 2-2.  Figure 2-3 shows a characteristic-powering scheme for a radio site.

Figure 2-1 A Powering Scheme for a Central Office

Figure 2-2 Typical Outside Plant Equipment Enclosure Power Scheme

Figure 2-3 Typical Radio Site Power Scheme

The principle components of the power distribution plant are:

- LOCAL AC POWER DISTRIBUTION —, which includes conduit, cabling, fasteners and protective equipment.  The PDSC is an Essential AC panel that feeds the rectifiers.

- CHARGING/RECTIFIER EQUIPMENT — consists of rectifiers and associated equipment to convert AC power to DC power at Voltages suitable for Qwest applications.

- TEMPERATURE COMPENSATION — and/or charge current limiting may be separate or an integral part of the charging equipment for use with VRLA batteries.  Temperature compensation measures battery temperature(s), and adjusts the plant Voltage accordingly to limit recharge current to the batteries thereby helping to reduce the risk of thermal runaway.  The temperature sensing is preferably done once per string on the most negative cell post of that string; and the control of the power plant float Voltage is adjusted based on the highest battery temperature measured.  Charge Current Limiting simply limits the available charge current to the batteries (either to prevent thermal runaway or prevent overload of the rectifier current limiting circuitry in the case of super™/ultra™ capacitors).

- STORAGE BATTERIES — provide a source of DC power to the equipment when AC is not present, until the AC can be restored.  They may also provide filtering of the rectifier output for some older types of rectifiers where the filtering wasn’t integral to the rectifier output.

- DISCHARGE BAYS — contain the control and output circuits; including fuses and/or circuit breakers, shunts, meters, bus bar, alarm circuits and other equipment necessary for plant operation.  May be the same as the PBDs described below.

- BATTERY DISTRIBUTION BOARD (BDB), or POWER BOARDS (PBDs) — is the primary power distribution within the DC plant (the originating PBD includes the controller).  It is powered directly from the batteries and rectifiers.  In addition, it contains the primary cable protection equipment, and shunts.  The BDB may also contain meters and alarms.  In some plants, these bays may contain any combination of one or more of the following:  multiple rectifiers (ferroresonant rectifiers 200 A and larger are often a bay unto themselves), the PDSC, the controller, the power monitor (if separate from the plant controller), primary distribution fuses and/or breakers, converter plants, and residual ring plants.

- SECONDARY DISTRIBUTION EQUIPMENT — is fed from the PDBs.  Secondary distribution includes Power Distribution Fuse Boards (PDFBs) for switches (they are known by many other switch-specific manufacturer names, such as LPDU, PD, PDF, PFD, GPDF, etc.), Battery Distribution Fuse Boards (BDFBs and BDCBBs), Area Bus Centers (ABC), and protective equipment.  The PBDs and secondary distribution equipment may be combined in smaller power plants.

- CONTROL VOLTAGE — is the Voltage used to operate alarm relays and control circuits in the power plant.  The primary Voltage of the plant should be the control Voltage.  This power is often provided off a small fuse panel called the Alarm Battery Supply (ABS).

- CONVENTIONAL CONTROL and/or POWER SYSTEM MONITOR CONTROLLER — there are two types of PSMCs used in Qwest.  Power System Monitor Controller - Central Office (PSMC-CO) and Power System Monitor Controller - Confined Locations (PSMC-CL).  It is preferred that the PSMC and the conventional controller be integrated into the same unit.  The Conventional Controller provides the interface between the rectifiers and the plant for "on and off" control under normal and adverse conditions.  Both the Conventional Controller and the PSMC may provide for rectifier and plant alarms, and contain the visual readout devices for operation of the plant.  They provide the means to assess the status of the elements of the power plant (with indications provided locally and remotely) that will permit determination of the impact of the alarm.  Monitors (PSMC-CO) for use in central offices shall be capable of TL1 communication (over X.25 or IP circuits) of plant alarms and any other alarms connected to them.  PSMCs also measure analog values, such as Voltages, currents, and temperatures.  PSMCs for Confined Locations (PSMC-CL) are used with VRLA batteries, are a “scaled-down” version of a PSMC, and may or may not be capable of X.25/TL1 communication.  All PSMC shall be capable of dial-up and be emulate a dumb terminal (i.e. VT100) on dialup or local serial access.

DC Grounding (and grounded) connections for electronic equipment locations shall be of the two-hole crimp (preferred), exothermic weld, or amphenol type (single-hole lugs are allowed for chassis grounds and for grounds where manufacturer specifications call for wire smaller than 14 AWG).  Mechanical connectors or connectors that depend solely on solder are not acceptable.

All DC power connections for both supply and return shall use crimp type copper connections and grade 5 steel nuts and bolts.  Connectors for direct battery connections are defined herein.  Aluminum connectors shall not be used.  Power connectors will be configured as follows:

•	Within the supplier's equipment, power connections will be configured to meet the supplier's requirements.

•	Between the supplier's equipment in the bay and the top of the bay, connections can be one-hole or two-hole crimp, depending on equipment design.

•	All connections to a battery return bus bar must be a two-hole crimp only.  Exceptions to the “two-hole” requirement are allowed for battery return bus bar rated at 50 Amperes or less.

Details for ground conductors can be found in Qwest Technical Publication 77355, "Grounding - Central Office and Remote Equipment Environment".

RHW, RHH or XHHW Class I stranding are the preferred DC power and grounding cables to be used in the Central Office power area (for wire sizes smaller than 14 AWG, TFFN is allowed as long as it is protected at all tie points and points of impingement).

All power equipment (including rectifiers, batteries, ring plants, fuse panels, etc.) to be used in Outside Plant equipment enclosures (e.g., CEVs, huts, Customer Premise sites, RT cabinets) shall be fully front accessible where rear access will be needed and the equipment does not have a rear aisle or rear access.

It is preferred that the shunt for power plants rated at 800 Amperes or larger be in the battery return (grounded) side of the charge/discharge bus bar.  For bus bar type and distributed type power plants (those without a remote chandelier), the shunt can be in the hot distribution and/or battery bus bar(s) located in the power board(s).

Low Voltage disconnect devices are normally only permitted in series with the battery strings, not in series with the load (see figures 2-1 and 2-2) except for DSL load-shedding (when it is only allowed in series with the DSL loads).   It is preferred that LVDs not be used at all (unless DSL load shedding cannot be accomplished by the DSL equipment itself).

## 2.3	Charging Equipment (Rectifiers), and their Controller

For proper plant operation, charging/rectification equipment shall have the following features or capabilities, whether they are required at the time of installation or not:

•	HIGH VOLTAGE SHUTDOWN — for ferroresonant rectifiers will occur when high Voltage on the DC output trips the high Voltage alarm and causes rectifier shutdown.  The high Voltage shutdown setting shall be adjustable.  Switch mode rectifiers’ HVSD is controlled by the plant controller.

•	REMOTE RESTART — allows a rectifier to be turned on from a remote location after high Voltage shutdown (usually be a ground signal on the R lead of the TR pair).

•	REMOTE STOP — permits rectifier shutdown.  Remote stop may be used during transfer from commercial to standby AC power or vice-versa or for energy management.  This is usually accomplished by a ground signal to the T (terminate) lead of the TR pair.

•	CURRENT LIMITING — protects the rectifiers/charging equipment when operating in an overload condition.  The current limiting circuit is normally designed so maximum output current will not exceed 120 percent of rating.  The current limiting shall generally be set between 100 and 110% (alarm threshold levels for rectifier overcurrent are provided in Chapter 13-5).

•	CURRENT WALK IN — controls the charging current from a gradual increase to full output.  This feature limits the surge of AC power required after AC power restoration and allows the control circuits to stabilize.  It typically takes at least 8 seconds for a rectifier to go from 0 to full load Amperes.

•	LOCAL OR REMOTE SENSING — refers to the point where the output Voltage is sensed for the feed back circuits.  Local sensing causes the rectifier to regulate the Voltage at its output terminals.  Remote sensing carries the regulation point to the battery terminals or some other selected point.  Remote sensing is the only type that is allowed in Central Office.  Under no circumstances will local and remote sensing be mixed in the same power plant.

•	AUTOTRANSFORMER — provides Voltage matching of the AC supply, maintaining the nominal design Voltage to the main transformers.

•	SEQUENCE CONTROL — provides the ability to turn rectifiers on sequentially, so that when AC is restored the load imposed upon the Standby engine or AC transformers by the rectifiers is sequential rather than block.  Sequence control will be provided from the power plant controller where it is necessary due to undersized engines or transformers, or due to improperly designed transfer switches (closed transition switches).  (See Chapter 8, Paragraph 8.5.)

•	PARALLEL CONTROL — is when all rectifiers are connected to the output DC bus at all load levels.  The capability of each rectifier to monitor battery Voltage individually and supply current on demand is called parallel control of charging units.

•	TEMPERATURE COMPENSATION — Rectifiers to be used with Valve-Regulated Lead-Acid (VRLA) batteries shall have slope temperature compensation charging features utilizing temperature sensors located at the batteries.  The compensation shall be capable of lowering the Voltage of the rectifiers to within one Volt or less of open-circuit Voltage at 55 degrees C (131 F).

•	VOLTAGE ADJUSTMENT — Rectifiers to be used with VRLA batteries shall be Voltage adjustable, both locally and remotely (e.g., sense leads).

•	ALARMS and ALARM SETTINGS — shall be in accordance with Chapter 13 of this publication.

For proper plant operation, rectifiers/charging equipment may have the following additional features depending on the system size and equipment served:

•	PROPORTIONAL LOAD SHARING — can be connected with other rectifiers and set to carry the load in proportion to the rating.

•	ENERGY MANAGEMENT — automatically places rectifiers above and beyond those needed to meet the load into hot standby.  This allows the remaining rectifiers to save overall plant kWhrs by having those rectifiers operate closer to full load (where they are more efficient at converting AC to DC).

•	PHASE SHIFTING — provides the ability for the AC input to be shifted to minimize the power factor in the AC input line (also known as power factor correction or PFC).

For single-phase switchmode rectifiers, the AC current total harmonic distortion (THD) reflected back toward the source must be limited to 15 percent at full load.  The third, fifth, and seventh harmonics must be 12 percent or less.

For three-phase switchmode rectifiers, the AC current total harmonic distortion (THD) reflected back toward the source must be limited to 35 percent at full load.  The third, fifth, and seventh harmonics must be 20 percent or less.

On power plants that use the controller to regulate the float Voltage, if the controller fails, the rectifiers shall default to 2.17 to 2.20 Volts per cell for floated batteries and 2.25 to 2.27 Volts per cell for VRLA batteries.

At startup, the total peak inrush current must not exceed ten times the steady state current requirement.

The power factor must be no less than 0.8 (80%) lagging or leading at loads of 10% or greater.

The acoustic noise shall be a maximum of 65 decibels audible (65 dBa), measured from a distance of two feet in any direction.

The DC ripple noise coming from the rectifiers shall be less than 35-decibel reference noise C-Message (35 dBrnC) and less than 300 mV peak-peak and 100 mV rms.

Rectifiers/chargers for use in hardened equipment locations shall be capable of reliable operation at operating temperatures between -40 degrees and + 65 degrees C (149 degrees F).

Any new rectifier should be capable of providing 60 V (for a nominal -48 V plant) or 30 V (for a nominal 24 V plant)

Each rectifier larger than 65 Amps must have its own dedicated AC connection.  One AC circuit cannot be use to power a rectifier shelf (unless the total shelf output capacity is less than 18 Amps nominal).  In customer premises and outdoor cabinet installations the shelf is often configured for two feeds, one for the even numbered rectifiers and the other feed for odd numbered rectifiers.

AC connections must be run in conduit or raceway.  Exceptions are for customer premises, where AC is provided by the customer.  Hard wiring is preferred, but twist lock type plugs are an acceptable alternative.  The worst case is a standard three-prong plug.  In those cases, a plug with a ground screw (or something similar to prevent the plug from being pulled out), should be used whenever possible.  If this is not possible, the Customer must sign a waiver absolving Qwest of liability in case of power plant outages (except for wall-mounted power supplies and equipment).

Green wire grounding (ACEG or “safety ground”) must be run with each AC rectifier feed for individually fed rectifiers.  For multiple rectifiers fed from one source, each AC feed shall have it’s own ACEG to the shelf or AC feed at the top of the power board.  All ACEG must be run in accordance with the NEC.

Bus bar type power plants must use a remote ground window (even if it’s only a few feet away), per Tech Pub 77355.

## 2.4	Engineering Guidelines

When sizing power plants, the following criteria shall be used:

•	List 1 drain is used for sizing batteries and rectifiers (generally a minimum 20% growth factor is also added to this).  List 1 is the average busy-hour current at normal operating Voltage.  Telephony List 1 drains are measured at 18 ccs for the first 2 hours of a discharge and 6 ccs thereafter, or at a constant 9 ccs.  For non-POTS equipment, the L-1 drain can be estimated as 25% usage/capacity.

•	List 2 drain is used for sizing feeder cables, circuit breakers, and fuses; the current that is required for projected peak under worst operating conditions (typically lowest Voltage with startup currents for capacitor charging and locked rotor fans) should be used.  Telephony List 2 drains are measured at 36 ccs (or 100% usage at worst-case loop lengths) at -42.75 V for a nominal -48 VDC plant.

•	List 3 drain is used for sizing converter plants.  The peak current that is required by equipment at a regulated operating Voltage should be used.  For loads with no variability, the average busy-hour current at normal operating Voltage should be used.

Collocator List 1 and 2 DC drains are not generally known, so the CLEC power request is used to size cabling, fuses/breakers (at a minimum of 125% of the request per feed), and DC plant components.

When a battery plant is initially installed, the meters and bus bar should be provided based on the projected power requirements for the life of the plant.  Base rectifiers and batteries should be provided based on the projected end of engineering interval connected average busy-hour current drains (List 1).

One more rectifier should be provided than the number required for the "average busy-season busy hour drain" needed at the end of the engineering interval (n+1) for base rectifier requirements.  The spare rectifier must be the largest rectifier in the plant.  (In COs, radio sites, or fiber regen sites, for non-individually fed rectifiers, the rectifier capacity of all the rectifiers that could be lost when a single AC breaker trips shall be used as the “largest rectifier”.)

Size the rectifier plant such that it will carry the office busy-hour load with a minimum excess capacity of 20 percent to recharge the batteries (1.20 recharge factor).  (For NNS and OSP sites, this factor should be 30% due to the higher float Voltage of VRLA batteries.)  The capacity of the working spare rectifier is included as part of the recharge capacity.  In addition, breakage of the rectifier sizing will usually provide a margin above the minimum 20 percent.  The minimum recharge factor will charge 4 hours of battery backup that has been nearly fully discharged back up to better than 90 percent of full capacity in less than 24 hours.  For small power plants in remote terminal applications serving 96 or fewer POTS-only customers, rectifier redundancy is not required.

Follow these general engineering guidelines:

- Main conductors and feeders in the plant should usually be sized for the ultimate capacity of the plant.  They should also be sized for a maximum temperature of 46 degrees C (115 degrees F).  (See Chapter 9 for more information on distribution cable sizing.)

- Rectifier and battery capacity should be added as the load grows.

- Charge/discharge or supplementary bays should be added only as needed.  The input cabling for these bays should be sized for the projected ultimate capacity (typically the bus bar Ampacity rating of the bay).

- Distribution equipment (fuses, or breakers) should be added only as needed.

- For power plants with rectifier sizes exceeding 65 A and VRLA batteries, the largest rectifier should be equal to or less than the total power plant load and recharge requirements.  If not, turn off excess rectifiers (leaving 1 spare on).  This will help to avoid extreme thermal runaway.

- For energy saving purposes, if total rectifier capacity exceeds the load plus the spare and recharge capacity, then all excess rectifiers should be turned off (either manually, with semiannual rotation into service; or by an automatic energy management algorithm from the plant controller).  These rectifiers should be turned back on when the load and recharge capacity requires it.  If the rectifiers are old, and/or at risk of capacitor dry out if turned off, don’t turn those off.

The shunt size of the plant (for plants with a main shunt in a chandelier arrangement) should generally be no more than twice the installed rectifier capacity to ensure accuracy of current readings.

Power cable racking in the power room shall be located in accordance with Qwest Tech Pub 77351.

All rectifier cables and any battery cables not protected by a breaker shall be considered as unprotected (un-fused) leads.  The charge leads shall be sized as follows for the rectifiers’ sizes listed:

The Voltage loop drop for the charge leads shall never exceed two Volts for the full loop.

- Leads to the charge bus for stand-alone 200-Ampere rectifiers shall be one 350 kcmil per battery and return.

- Leads to the charge bus for stand-alone 400-Ampere rectifiers shall be two 350 kcmil per battery and return.

- For smaller rectifier sizes (or the rare 800 A rectifier), follow manufacturer recommendations for the leads to the charge bus.

- For rectification bays/shelves, follow the manufacturer recommendation for the leads to the charge bus, ensuring that the Ampacity of the cables used exceeds 120% of the rectifier shelf/bay capacity, and that the Voltage drop does not exceed two Volts for the loop.

- Rectifier output leads over 125 feet one-way shall be sized using the manufacturers’ recommendations (where available), ensuring that the Voltage drop does not exceed two Volts for the loop.

## 2.5	Power Board Panel and Fuse Numbering for New Power Plants

This requirement is for new power plant panels and fuse numbering to accommodate COE-FM and NMA requirements.  Existing power plants will continue with the existing numbering system, and are not affected by this requirement.

New power plant distribution bays will have panel labeling starting with Panel 01 (PNL-01) from the bottom in each bay to Panel XX (PNL-XX) at the top of the bay.  Each panel’s fuse positions will start with Fuse 01 (FS-01) to Fuse XX (FS-XX), which would be the last fuse number of that panel.  This will allow fuse panels to be removed or added and not affect the fuse numbering in the bay.  If multiple panels exist on a given level numbering will start in the lower left corner of the bay with PNL-01 proceed left to right on that level with PNL-02 then proceed up and left to right for additional panels in the bay.  Fuses will be labeled left to right or top to bottom depending on the panel’s orientation.  Fuse positions will be assigned in the power boards from the bottom up.

To satisfy the NMA requirements in the power monitor, a unique 7-digit number will be created as follows:

- 1st digit “P” for power plant bay

- 2nd and 3rd digits will be the last 2 digits of the bay number (P0101.03)

- 4th and 5th digit will be the panel number (PNL-04)

- 6th and 7th digit will be the fuse number on that panel (FS-08)

- For the example shown above, the NMA identifier would be P030408.

  - When the installer is ready to test fuse/breaker capacity alarms for the new NMA numbering of the Power Board panel and fuse, mention to the technicians in the NMA database group that these distribution numbers are not template generated and need to be manually databased.

In distributed power bays where rectifiers and distribution exist in the same bay, rectifiers are labeled as G-01 to G-XX in that bay from the bottom to top, left to right, as required, and continue with the next consecutive rectifier number in additional bays.  The distribution panels will start with Panel 01 (PNL-01) wherever the first distribution panel starts in that bay and is then labeled from bottom to top.  In additional bays, the distribution panels will always start with Panel 01 (PNL-01) where the rectifiers will continue with the next consecutive rectifier number.

Specific examples are shown in the Qwest configuration (Q&A) help files for a particular power plant.  This aid is to help and assist planners, engineers, installers, and suppliers.

## 2.6	Conventional Controller

The traditional power plant controller shall be capable of basic alarm and control functions as described below.  In most COs, the alarms will be connected to an “intelligent” power monitor/controller (PSMC) as described in Chapter 8.

All provided alarms must be capable of being monitored remotely.  The connecting point for these contacts will be easily accessible.  All analog monitoring points (current shunts or Volt meters) within DC plants larger than 100 A of capacity will be equipped with terminal strip access for attaching remote monitoring devices.  The connecting point for analog monitoring points will be located near the alarm connecting points and be easily accessible.  Binary alarm thresholds from analog points shall be settable.  The following alarm indications shall be provided:

•	Power Minor Alarms

  - Rectifier failure - single rectifier failure

•	Power Major Alarms

- Discharge fuse

- High Voltage

- Low Voltage (below battery open-circuit Voltage)

- Voltmeter and Voltage regulator fuse

- Charge fuse

- Rectifier failure - multiple rectifier failure

•	Power Critical Alarms

- Very low Voltage

When the power plant controller and the power monitor are separate entities, the power plant controller major and minor alarms should be paralleled with the PSMC major and minor on the e-telemetry device or switch in case the PSMC fails.

Control functions of a traditional controller will be limited to high-Voltage shutdown and restart capabilities, as defined herein; and rectifier sequencing.

Plant controllers for 50 Ampere plants and larger must have digital Voltage and current meters (this may be a combined meter).  Power plants with a capacity of less than 50 Amperes are not required to have a meter, but shall have test jacks so that the plant Voltage and current can be measured with a meter.

Rectifiers whose outputs are controlled by the power plant's controller must default to the rectifier's settings if the controller fails.

CONTENTS

Chapter and Section 	Page

3.	Batteries	 3-1

3.1	Overview	 3-1

3.2	General Description	 3-1

3.3	Battery Discharge Characteristics	 3-1

3.4	Battery Recharge Characteristics	 3-3

3.4.1	Ventilation of Battery Areas	 3-4

3.5	Battery Configurations	 3-5

3.6	Battery Types	 3-6

3.7	Selection	 3-10

3.8	Sizing	 3-10

3.9	Battery Stands and Connections	 3-11

3.9.1	Metal Stands, Trays, and Compartments/Boxes	 3-11

3.9.2	Round Cell Stands	 3-12

3.9.3	Battery “Stand” Installation	 3-13

3.10	Battery Disconnects	 3-18

Tables

3-1	Typical Battery Disconnect Sizes for Flooded Cells	3-19

Figures

3-1	Typical Arrangement of Cables for a Battery Stand	3-16

3-2	Minimum Dimensions for a Bus Bar Above Battery Stands	3-17

# 3.	Batteries and Battery Stands

## 3.1	Overview

This unit covers requirements for batteries and battery stands used within telecommunications facilities.

## 3.2	General Description

During short term commercial alternating current (AC) disturbances, telecommunications equipment is operated on the direct current (DC) reserve power typically supplied by batteries.  The reserve battery power required for telecommunications sites with lifeline service are 4, 8, or more hours, as described herein (non-lifeline services, such as DSL, are not held to any battery backup standard).  During normal AC power operation, batteries are maintained in a fully charged or float condition.

Some computer systems, such as Operational Support Systems and data processing centers, require an Uninterruptible Power System (UPS) to furnish continuous AC power to their loads.  The UPS consists of chargers and inverters with an associated battery reserve.  Reserve time for UPS systems is typically 15-45 minutes, although it can be more or less.  This allows uninterrupted operation through brief power disturbances or, if necessary, provides the time for a smooth shutdown or transfer to a standby AC source.  A UPS system with less than 4 hours of battery backup shall NEVER be used as backup for telecommunications Network loads critical to ensuring Network lifeline operations.

All materials used in battery cases shall have a minimum limiting oxygen index (LOI) of 28% (per ASTM standard D2863), and meet the UL-94 V0 burn requirement.  Battery cases shall have sufficient strength to withstand normal handling and internal pressure generated by positive plate growth (within their design lifetime) and/or discharging and recharging.

## 3.3 Battery Discharge Characteristics

Battery strings designed for use with standard DC Central Office plants provide at least 4 hours of reserve time.  On discharge, as a lead-acid battery initially supplies the load current, the Voltage will rapidly drop, then levels out, (turnaround Voltage) before rising to a slightly higher Voltage (plateau Voltage) before beginning to fall again.  This phenomenon is referred to by the term “coup de fouet” (crack of the whip).

During the remaining discharge time, the Voltage falls slowly until the "knee" of the discharge curve.  After this point, further discharge results in rapid drops in Voltage caused by rapid electrochemical depletion of the cell.  Plots of "initial Voltage" versus discharge Amperes are available from battery suppliers as either separate curves or part of the normal discharge curves.

A plant and its loads are designed to operate to minimum discharge Voltages between 1.90 to 1.75 Volts per cell (also known as end Voltages or cut-off Voltages) for lead-acid cells.  Voltages below 1.75 on a long duration discharge can indicate a reversed (non-recoverable) cell.  The MVPC (minimum Volts per cell) for chemistries other than lead-acid is determined from the end Voltage of the equipment, (typically no higher than 
-42.75 V for nominal -48 V equipment) plus the Voltage drops defined in Chapter 9, divided by the number of cells per string.

The coup de fouet Voltages, and the Voltage at the knee of the discharge curve are dependent on the discharge current, type of cell, float Voltage, and the amount of time since the last discharge; and they are generally lower at higher discharge currents relative to battery capacity.

A fully charged (1.215 specific gravity) lead-acid wet/flooded cell has an open circuit Voltage of about 2.06 Volts after a day or two off of charge (this will decrease with time off charge).  The "calculated" open circuit Voltage of a lead-acid battery can be found by adding 0.85 to the specific gravity of the electrolyte of that battery.  The minimum recommended float Voltage could be found by adding 0.95 to the specific gravity (the bare minimum Voltage needed to keep the cell charged is a little less than this).

The highest Voltage reached during a discharge after the lowest coup de fouet Voltage is sometimes referred to as the plateau Voltage.  The lowest coup de fouet Voltage is sometimes called the turnaround Voltage.

Batteries shall be floated and alarmed at the levels prescribed in Chapter 13.  Exceptions to this include flooded batteries that are installed in some old WECO 100 or 300 series plants with their original controller.  They should generally be floated at 2.17 Volts per cell due to the inability to change some alarm and HVSD thresholds in these plants.

The first and last cells of a flooded battery string will not be in adjacent positions on the same shelf.  The first and last cells of a battery string must be either on opposite ends of the same shelf or on separate shelves.  Cell 1, the positive end of the string, shall be located on the lower tier (on two-tier stands where a string uses both tiers).  Exceptions are allowed for small VRLA batteries rated at 130 Amp-hrs or less, which can be on the same shelf and adjacent in some battery tray configurations.

Follow the manufacturers’ recommendations for installation of all batteries.  Each cell in the battery string shall be numbered, unless it is a monobloc (multicell battery) with an opaque jar.  The numbers should be placed on the battery stand under the corresponding cell where possible, or on the battery if that is not possible.

## 3.4	Battery Recharge Characteristics

A float Voltage of 2.20 Volts per cell, for flooded type lead-calcium, nominal 1.215 s.g. batteries, available from rectifiers in typical DC plants, not only maintains the batteries at full charge, but also recharges them after discharge.  Whenever the DC plant and the equipment being served will accept a power plant Voltage by floating the batteries at 2.20 Volts/cell (as opposed to the older 2.17 Volts/cell typically used for lead-antimony batteries), the higher float Voltage should be used.  This higher float Voltage will result in reduced maintenance and longer battery life.

If an office loses commercial power and is required to use battery power for several hours, the batteries must be recharged when commercial power returns.  If the rectifiers can deliver much more current than the load requires, the batteries will recharge quickly.  However, there is a danger in having too many rectifiers for certain battery types.  If the batteries recharge very quickly, they are receiving a lot of current.  Because of the internal resistance of the battery, heat is generated when current passes through the battery, on either discharge or recharge.  If too much current passes through the batteries, some older VRLA batteries are not able to dissipate all of the heat, and may go into thermal runaway.  Also, Li-based batteries have a charge current limiting circuit that may disconnect the batteries if too much charge current is flowing to them.  Therefore, it is unwise to oversize the rectifiers to recharge the batteries quickly.  Use the n+1 and 120% rules described in Chapter 2 for proper rectifier sizing to the load, and recharge.  As a general rule do not leave more than 200% of the load in rectifier capacity turned on (lockout/tagout excess rectifiers) unless it is necessary to meet the n+1 and 120% recharge rules.  Recharge time will be lengthened when current limiting or temperature compensation is used with VRLA batteries.  Although this slightly compromises reliability, safety concerns necessitate the use of these devices.

New flooded cells are given an initial boost charge at a relatively high Voltage to help finish “formation” of the plates.  This charge usually lasts several days (follow manufacturer recommendations), and care must be taken to prevent a buildup of Hydrogen gas in the battery area.  In addition, individual cells may sometimes become weak (with a depressed Voltage and/or specific gravity) over time.  Sometimes boost or equalize charging (equalize charging is very similar to boost charging) for the string or for individual cells may bring these weak cells up to proper float Voltage.

Boost charging is also sometimes used on flooded cells to recharge the batteries quickly if they have recently experienced multiple deep drains and there is a fear that there are more commercial AC outages pending in the near future.  Boost charging is commonly used in solar/cycling/photoVoltaic applications.

Valve-Regulated (VRLA) batteries are much more susceptible to thermal runaway at high Voltages than are flooded cells.  For this reason, all plants equipped with VRLA batteries going forward must employ temperature compensated charging.  Preferably, there will be one cell/monoblock monitored per string (typically the most negative cell/monoblock in the highest row of the string), with the highest temperature determining the float Voltage compensation.

VRLA batteries are also sometimes contained in a relatively confined space, enabling the buildup of volatile concentrations of Hydrogen gas during thermal runaway conditions.  For thermal runaway reasons, boost (including initial boost) and equalize charging of VRLA batteries is strongly discouraged.  These batteries can be placed in service and will finish plate formation and recharge over time (they also receive a better formation charge at the factory than a flooded cell).  Safety takes precedence over having a fully-charged battery all of the time.  If boost or equalize charging is done to VRLA batteries, ensure that manufacturer’s recommendations are strictly followed, and the batteries are checked on frequently for abnormal heating or gassing.

Note that not all lead-acid batteries are designed with the same types of plates.  UPS and engine start batteries typically have thinner plates (thus they can get current out quickly in a smaller footprint but won’t last as long), and VRLAs used in UPS or engine-start applications are typically of the AGM type (see Section 3.6).  Cycling/solar or engine-start batteries may have antimony in the plates, or other special manufacturing methods to ensure at least 800 cycles to an 80% depth-of-discharge.

### 3.4.1	Ventilation of Battery Areas

All aqueous batteries (such as lead-acid and Ni-Cd) gas potentially explosive Hydrogen; especially during thermal runaway, boost charging, or equalize charging.  Under normal float operating conditions, flooded cells will gas much more Hydrogen than a VRLA battery (under normal operating conditions, the VRLA battery should be recombining much of the Hydrogen with Oxygen to replace the water).  However, during the first year of service for VRLAs (especially for gel technology), the VRLA may gas the same amount as an equivalent flooded cell.  In addition, under thermal runaway conditions VRLA batteries are capable of gassing incredible amounts of Hydrogen; and under extreme thermal runaway conditions; they may even gas potentially toxic Hydrogen Sulfide.

Because of these potentially toxic and explosive gasses, it is very important to ensure that battery rooms/compartments/areas are adequately ventilated.  Hydrogen buildup in battery rooms/areas or compartments should be limited to approximately 1% (the LEL — Lower Explosive Limit — of Hydrogen is 4%).  This applies to battery rooms as well as battery compartments in cabinets.

As a minimal guideline, Qwest has adopted a minimum air change rate of 0.5 ach (air changes per hour), unless other calculations are done ensuring that Hydrogen concentrations do not exceed 1% under boost charge conditions (this is a Fire Code requirement).  In the great majority of cases, 0.5 ach will ensure that Hydrogen concentrations do not exceed 1% (see IEEE/ASHRAE 1635 for gassing and ventilation calculation methods to meet Fire Code requirements).  Note also that normal occupancy calculations require even greater than 0.5 ach for “occupied” rooms.

For Customer Premise cabinets, both the cabinet itself and the surrounding room should meet the air change and Hydrogen buildup guidelines.

Engineers typically do not prefer to design excessive air changes into the ventilation system, as this would compromise thermal efficiency of the HVAC system, especially in hot or cold climates.  In some cases, redundancy and/or DC-powering are designed into the ventilation system to ensure that there will always be minimal ventilation.

Some “confined space” applications (like CEVs) also require alarming or testing before entering for toxic and explosive gasses (as the Hydrogen vented by batteries).  The alarm levels are set by OSHA and are outside the scope of this document (more information on gas monitoring can be found in Telcordia GRs 26 and 27).

Note that Li-based batteries do not gas, and thus do not require ventilation (although if they are used in “people space” there must be ventilation for personnel).

## 3.5	Battery Configurations

The general descriptions of a battery plant, its configuration, sizing guidelines, etc. are given in Chapter 2.

CAUTION

Cells with different specific gravities and float Voltages cannot be mixed.  For example, VRLA and flooded cells cannot be placed in the same string.  The VRLAs will sit essentially at open circuit and self destruct in a relatively short time.  Different string sizes and different battery manufacturers may be used in the same battery plant.  However, this is discouraged for VRLA batteries.  Cells of different sizes and/or different manufacturers shall not be used within the same battery string, unless the battery is no longer manufactured; in which case consult the manufacturer for suitable replacement alternatives.  If replacement alternatives do not exist, then the entire string must be replaced.

## 3.6	Battery Types

Qwest uses several battery technologies in equipment locations.  The characteristics and requirement of the battery types are not always interchangeable.  The Qwest Engineers are responsible for the sizing of the battery reserve of a site.  The battery technologies used in Qwest are:

- FLOODED LEAD ACID — flooded (also known as wet or vented) lead-acid batteries are the "traditional" batteries used in large telecommunications equipment locations.  This group of batteries includes the pure lead, lead-antimony, and lead-calcium battery types.  Lead-antimony batteries are not to be used by Qwest going forward except in engine-start and cycling (solar/photoVoltaic) applications.  If it is feasible to use flooded batteries, they should be used.  Lead-calcium is the preferred battery type for long duration float applications.

In a lead-antimony cell, antimony is added to the lead plates in a conventional lead-acid storage battery design to add mechanical strength.  As these batteries age, they develop higher and higher self-discharge rates, require higher trickle currents, and need greater maintenance because of higher water loss from gassing than other flooded lead-acid cells.  A 1680 Ampere-hour lead-antimony cell takes 550 to 650 milliamperes of float current when new, and 1100 to 1300 milliamperes when approaching the end of life.  The Ampere-hour efficiency, calculated by dividing the Ampere-hours of discharge by the Ampere-hours required to restore the cell to full charge, is lower for these cells than for most other types.  The average expected life on float at 77° F is 14-15 years, based on experience.  (When these batteries start using an appreciable amount of water [over half a gallon per month], they must be replaced immediately!)

The lead-calcium cell design results in lower self-discharge, lower trickle charge current and less maintenance than the lead-antimony design.  However, the condition of the cell is more difficult to determine using specific gravity and Voltage readings because of the lower gassing rate and; therefore, limited electrolyte gravity change.

In float operation, the cells take 60 to 300 milliamperes of float current for a 1680 Ampere-hour cell.  Experience has shown an average life on float at 77° F of 18-20 years.

Lead-calcium and lead-antimony cells shall not be used in the same string due to differences in charge/discharge rates, and the possibility of electrolyte contamination from hydrometers, etc.

The pure lead flooded cell is designed to minimize the physical deterioration associated with conventional designs.  The float current range for these cells is similar to that for lead-calcium cells.  The expected life on float of the second generation of these cells at 77° F is better than 40 years.  The pure lead flooded cell is also known as the “round” cell, or the “Bell” cell.  (There are also pure lead and pure lead-tin VRLA designs, and while they won’t last 40 years, they will last longer than other VRLA alloys in float service.)

- VALVE REGULATED — Valve-Regulated Lead-Acid (VRLA) batteries include both the starved electrolyte (absorbed glass matte or AGM), and immobilized electrolyte (gel) technologies.  Starved electrolyte shall not be used in Qwest Local Network (LNS) Central Offices.  A "characteristic problem" of valve regulated batteries is the potential for thermal runaway.  Suppliers of VRLA batteries will provide "safe operating environment" characteristics with VRLA batteries.  VRLA batteries require a higher float Voltage than flooded lead acid batteries.  Rectifier plants supporting valve-regulated batteries should be able to sustain a float Voltage of up to 2.35 Volts per cell.  VRLAs shall not be boost or equalize charged unless they have not been charged for at least 6 months.  In those cases' follow the suppliers’ recommendations for charge times and charge Voltages.

For -48 Volt plants, twenty-four battery cells should be used for each string wherever possible.  This also applies to +24 Volt plants, where twelve battery cells must be used for each string.  Two strings minimum are required for VRLA batteries except when used to backup only DSL, or for POTS-only RTs or Prems serving 96 or fewer customers.  Dummy cells are not permitted for use within Qwest.

- NICKEL CADMIUM — Ni-Cd batteries used within Qwest are generally based on a flooded technology.  Because of their relatively small size, cell Voltage difference, and high cost, nickel cadmium battery use is generally limited to standby engine-alternator start and control batteries in higher temperature environments, or cycling/solar batteries in low temperature environments.  Lead-acid cells are also used as start or control batteries for engine-alternators in Qwest Equipment.

- NICKEL-METAL HYDRIDE (NMH) — Like Ni-Cd, NMH (or NiMH) is an alkaline (potassium hydroxide electrolyte, which means it must be neutralized with an acid instead of the typical baking soda basic solution used for lead-acid batteries) chemistry.  Alkaline chemistries generally have a nominal Voltage of 1.2 V/cell (as compared to nominal 2 V/cell for lead-acid chemistries and 3-4 V/cell for Lithium chemistries).  The actual charging and open-circuit Voltages for NiMH cells are very similar to those of Ni-Cd cells.  Often, the individual cells are pre-packaged into a nominal 12, 24, or 48 V monobloc.  Nickel-metal hydride cells have been deployed as a longer life alternative to lead-acid cells in some distributed power constant current charging OSP applications, and are under consideration (along with Li-based batteries) for constant Voltage applications where they can save space and weight.  Temperature compensation must be employed when these batteries are used with traditional telecom constant float Voltage rectifiers.

- LITHIUM — The sealed nature of Li-based batteries eliminates traditional concerns of out-gassing.  Construction of battery modules in integral 48 or 24 V monoblocs eliminates the series connection of modules to achieve the required plant potential.

There are two primary types of lithium-based batteries.  One is Lithium-ion, and the other is Lithium-metal polymer.  Lithium-ion (Li-ion) has been popular for portable applications (cell telephones, camcorders, laptops, etc.), and is presently in the early stages of deployment for larger stationary applications incorporating both high rate and long duration discharge applications (note that like lead-acid cells there are internal differences between high-rate and long duration discharge cells).  A Li-ion cell consists of lithium ions imbedded in a carbon-graphite substrate (positive plate) or a nickel-metal-oxide, or a polymer phosphate.  The electrolyte is a liquid carbonate mixture, or a gelled polymer.  The lithium ions are the charge carriers in the battery.

Lithium-metal-polymer (LMP) is an even newer technology, but is further along in its deployment for stationary applications.  LMP batteries use thin film lithium metal for the positive plate, and a vanadium oxide negative plate.  These are encased in a polymer (plastic-like) electrolyte.  The solid polymer electrolyte must be heated (to about 140 degrees F) to achieve the most efficient flow of electrons.  This is done with internal heaters fed from the battery energy or charge current.

There is no gassing, no free electrolyte, and no hazardous materials with Lithium batteries.  LMPs work well in high-temperature environments, but Li-ion batteries are better suited for indoor environments.  Li-ions can usually be used in OSP applications with reduced life in high-temperature environments.  The shelf life of most Li batteries is 2 years plus, provided the parasitic loads of the built-in charge-control circuitry are put to sleep.

The drawback to Lithium is that it is an extremely reactive metal (it reacts in free air).  This means that sealing the battery and controlling the charge current are very important.  Controlling the charge current is done quite well with electronics imbedded in the battery.

Due to the electronic charge current controls, the newness of the technology, and the clean-room manufacturing environment, Lithium-based batteries are more expensive initially than their lead-acid counterparts.  However, where gassing, high-temperature environments, space, or weight are an issue, lithium batteries can pay for themselves in 6 years or less.

Lithium-ion based cells have a charge Voltage of between 3.4 and 4.1 V (depending on chemistry).  However, charge Voltages too close to the top end shorten battery life, while those closer to the bottom end reduce capacity.  Open circuit Voltage for these cells is 0.05 V below the charge Voltage.  Expected life for stationary Li-ion batteries is expected to be 15-20 years (regardless of environment), with a minimum of 10, and possibly a maximum of 25 or more years.  The cells may be cylindrical (spiral-wound), and typically packaged in series "blocks" to achieve higher individual module Voltages.  In some cases, these monoblocs may be packaged in rack-mountable metal-encased "shelves" that can mount in a relay rack.

LMP cells have a charge Voltage of between 3.0 and 3.1 V/cell (temperature compensation should not generally be used on Li-based batteries).  The open circuit Voltage is the same.  Expected life for these batteries is expected to be around 27 years (regardless of environment), and they are warranted for full replacement up to 10 years.  These are rectangular batteries, and the cells are "stacked" in series to achieve the desired module Voltage.

- SUPER™/ULTRA™ CAPACITORS — Electric double charge layer capacitors (commonly known as super™- or ultra™-capacitors) using carbon-based electrodes have made capacitances of thousands of Farads possible in small, packages.  For very short duration discharges (less than a few minutes), they provide an economic alternative to batteries.  Generally, due to their extremely low internal resistance, they must be coupled with a DC-DC converter or a charge current limiter to be used with existing DC plant rectifiers.

## 3.7	Selection

The selection of battery type and size for an installation depends on:

- Initial busy hour load and estimated growth pattern with time

- Added Power failure loads (such as AC-preferred inverters and switched DC lighting)

- End Voltage per cell

- Office reserve requirements

- Battery aging characteristics

- Ultimate Power Plant size

- Temperature

- Environmental constraints

For a new plant, the optimum battery stand and floor layout is achieved by using only one battery model.  However, strings of different types and sizes may be mixed.  The Qwest engineer will determine the type and manufacturer of the batteries to be used.

In RT cabinets, where the temperature of the battery compartment will regularly drop below 30 degrees F in the winter, battery heater pads should be installed where lead-acid batteries are used.  They normally operate when the temperature is below 40 degrees F, and normally do not operate when the temperature is above 50-60 degrees.

## 3.8	Sizing

At least 4 hours of battery reserve shall be provided for sites serving lifeline POTS with a permanent on-site auto-start, auto-transfer engine (this reserve can be reduced to an hour for traditional CATV sites with an engine).  Sites served by a portable genset that serve lifeline POTS loads shall have at least 8 hours of battery reserve, unless they have a host, tandem, standalone, or long distance switch, in which case they shall be equipped with a permanent auto-start, auto-transfer engine, or contain at least 24 hours of battery backup.

Customers at Prem sites have the option of less or no battery backup (see Tech Pub 77368 for further information).  DS-1 and faster services for cellular/PCS can have as few as 4 hours of backup (even without an engine) since that is normally the backup provided by the wireless company for themselves.

DSL services may or may not be backed by batteries (or super/ultra™ capacitors).  If it is backed up, it is often for times around 5 minutes.

Radio sites that are inaccessible during parts of the year should have more than 8 hours of battery reserve (determined by the Common Systems Power Planner in consultation with field personnel).  Sites solely solar power should have multiple days of battery reserve, depending on the climate.

Lead-acid batteries shall be sized using an end Voltage of 1.86 Volts per cell for LNS CO sites (1.85 is an option for OSP sites), and 1.88 Volts per cell for NNS sites.  (For the rare 23-cell VRLA strings, 1.93 Volts per cell must be used for sizing)

Lithium batteries have a discharge current limit linked to an internal disconnect.  When sizing a plant using Lithium batteries, it is essential to ensure that a loss of a single battery will not cause the other batteries to exceed their discharge or recharge current limits.  If these limits are exceeded, an additional battery must be added.  In cases of plants where Lithium batteries are paralleled with lead-acid batteries, at points during the discharge and recharge cycles, the Lithium batteries will be supplying or receiving almost all of the current.  As a result, sizing must take this into consideration so that the internal disconnect of the Lithium battery is not operated.

Lithium batteries in -48 V plants in COs should use an end Voltage of -44.45.  In the OSP, they can use an end Voltage of -44.

## 3.9	Battery Stands and Connections

### 3.9.1	Metal Stands, Trays, and Compartments/Boxes

Metal battery stands are available in a variety of configurations to suit power room applications.  The stands are steel finished with acid-resistant paint.  Shelves of battery stands for flooded cells should be protected by a non-conductive, acid-resistant, plastic sheet under the batteries.  The engineer should follow all the specifications pertaining to battery equipment installation to avoid hazardous conditions resulting from abnormal stress, chemical corrosion, or electrical faults.  Large VRLA batteries are generally mounted with the terminals facing forward in large metal powder-coated battery stands.  The stand used must be designed for the battery used, installed according to manufacturer instructions, and rated for the Earthquake Zone in which it is used (an existing stand that is not earthquake rated may be re-used in place if the earthquake zone of the site is 0, 1, or 2).

Battery trays that mount in heavy-duty relay racks are also made of metal.  They must be rated for the weight they will support, and specify the number of screws needed for the weight supported.  The shelves should be powder-coated, and may optionally be protected with a non-conductive, acid-resistant plastic sheet.

Very small batteries may mount in a powder-coated metal box that may be wall or relay rack mounted.

In outdoor RT cabinets, batteries are housed in metal trays and/or battery compartments.  If housed in sliding drawers, the drawer slides shall be rated for the weight they will carry, and the top clearance between the battery posts and the compartment above shall be at least ½“ (the battery posts should be protected with insulating covers if the clearance is less than 2”).  The trays and/or compartments may be powder-coated, and should have a heater pad for climates where the temperatures will regularly drop below 30 degrees F in the winter, and lead-acid batteries will be used.  The heater pad should keep the batteries to a temperature of at least 40 degrees F, but not be active at battery or ambient temperatures above 60 degrees F.

All battery stands and relay racks equipped with battery trays that don’t have battery disconnects should be grounded with a #6 AWG ground wire.  For battery disconnects rated 15 A and smaller, a #14 AWG ground wire to the metal box may be used.  For 20 A battery disconnects, a #12 AWG may be used.  For 25-60 A disconnects, a #10 AWG may be used.  For 70-100 A disconnects, a #8 AWG must be used.  For 110-200 A disconnects, a #6 AWG is required as a minimum.  For 225-300 A disconnects, a #4 AWG is required for stand grounding.  For 350-500 A disconnects, a #2 AWG minimum is required.  For 600-800 A disconnects, a 1/0 AWG grounding conductor is necessary.  For 1000 A disconnects, a 2/0 AWG ground is needed.  For 1200 A and larger disconnects, ground the stand with a 4/0 AWG.

### 3.9.2	Round Cell Stands

A modular polyester-fiberglass battery stand is available for use with pure-lead flooded round cells.  These types of stand are acid-resistant, fire retardant, and eliminate the possibility of a ground fault or an electrolyte path between cells of widely different Voltages.  These stands are not recommended in Qwest on a going forward basis because they limit the engineer's choice of battery manufacturers for the life of the stand.  Although the stands are not metallic, a #6 AWG ground wire should be run to them to allow a place for a technician to discharge static electricity before working on cells.  If a polyester-fiberglass round cell stand has integrated rack spill containment (available on some newer designs), and that is the only type of stand in that DC plant, other types of spill containment (such as room containment) are not required.

New polyester-glass stands must be rated for the Earthquake Zone in which they are placed.  Older round cell stands may be re-used only in Earthquake Zones 0, 1, and 2.  The 3rd tier of a 3-tier round cell stands shall not be re-used.

### 3.9.3	Battery “Stand” Installation

Battery stands must be placed in accordance with Qwest Technical Publication 77351.  Single sided battery stands must not be placed closer than 6 inches to any wall, post, or pillar.  All other battery stands shall follow aisle requirements stated in Qwest Technical Publication 77351.  The battery side of two-tier two-row battery stands must not be placed next to a wall; however the end can be placed near the wall using the spacing requirements found in Pub 77351.

Spacing requirements for battery bays (heavy duty relay racks) equipped with VRLA or Li-based batteries are not covered by Tech Pub 77351 however.  These bays do not need rear or side clearance, although rear access is desirable if the batteries are top terminal batteries installed in a stationary tray.  Front clearance for battery bays where the installed batteries will not exceed 85 lbs. apiece is only required to be a minimum of 2 feet.  However, for batteries weighing more than that, 3 feet is the desired minimum front clearance, and 30” is the required minimum.

Two intercell connectors should be used in all applications where battery posts are designed to accept multiple intercell connectors.  The thickness of the connectors should be designed so that the connector(s) will have sufficient strength and flexibility for earthquake zone 4.

All nuts and bolts connections made to battery posts, terminal plates, and intercell connectors shall be made with stainless steel (preferred), lead, or lead coated copper.

Intercell connectors, inter-tier connectors, inter-row connectors, terminal plates, and all connector lugs connected directly to the battery posts shall be lead or lead coated copper.  Lead plated connector lugs do not have to have an inspection window.  All other lugs should have an inspection skive.  Tin-plated copper compression type lugs can be used when connecting to the terminal plates; however they cannot be used to connect directly to the battery posts.  The installer is to cut off any connector lug that does not have the inspection hole and install the correct lug, even if the lug is supplied by the battery manufacturer.  There will be no connectors varnished, Karo™-syruped or painted, during or after installation.

For any lug within two feet of a battery vent, it is desirable to use heat shrink tubing around the connection to attempt to seal it from corrosive vapors.  However, it may only be clear heat shrink tubing so that if it is not perfectly sealed, the corrosion can be noticed.

During activities that could result in an acid spill, including the installation, removal, or rearrangement of batteries, sufficient acid neutralization material shall be on hand to neutralize and contain a minimum of eight gallons of acid for large flooded batteries, or one gallon for flooded engine-start batteries.

All battery stands shall provide means for anchoring to the floor in order to meet Qwest earthquake Zone standards as required.  The Qwest approved battery stand anchor shall be used except when shimming is required.  The approved Qwest toll anchor shall be used when shims are necessary due to uneven floors.

Battery strings should use alpha designations (A, B, C, etc.).  The letters:”O and I” should not be used.

Battery strings are to be connected in parallel, and individual batteries within a string are to be connected in series.  Individual cells will not be connected in parallel externally; however multiple cell batteries can be connected in parallel within the battery case.

Lead-calcium batteries shall not be reused in another site if the cells are older than 5 years from the manufacturing date on the battery.  Pure lead round cell type batteries with a list number of L-1S, L-2S, L-3S, or L-4S may be reused in another site if they are less than 15 years old.  Any round cell that has a list number ending without the “S” shall not be reused for any reason.

New and significantly remodeled battery rooms must conform to the provisions of the Fire Code); be compartmentalized (for lead-acid batteries), and have acid spill containment if the total free-flowing liquid electrolyte exceeds 1000 gallons (or if so ordered by the Fire Marshal or Building Inspector).  Where containment is necessary, whole room containment is preferred within Qwest, however if this is not practical, area containment is the next option; with individual stand containment as the least desirable option.  Unless specifically ordered otherwise by the Fire Marshal, neutralization and/or absorptive pillows are not required under the battery stands (they are in the spill kits in the battery area for reactive response).

The bus bar, auxiliary framing, or cable rack, shall be a minimum of six inches directly above the highest point of the battery.  No framework, cable racking, bus bars or any other obstruction shall not interfere or impede with the maintenance of the batteries.

Battery bus bars over flooded battery stands (except the chandelier) may be stacked as long as the following requirements are met.  The battery feed bus bar shall be located a minimum of one foot above the cable rack.  The battery return bus must be located a minimum of six inches below the cable rack.  Battery bus bar shall not be stacked on the same side of the cable rack when above battery stands (however, when not above battery stands, they may be on the same side of the cable rack as long as the vertical separation between busses of opposite polarities is at least 6 inches).  When the bus bar is not stacked, the bus bar shall be a minimum of six inches below the cable rack.  If there is insufficient room to place the bus bars below the cable rack the battery termination bars may be installed a minimum of four inches above the cable rack.  There must also be a separation of eighteen (18) inches minimum (center line to center line) between the battery and return buses (see Figure 9-5) when they are installed in the horizontal plane by each other.

Sizing of the cables from the bus bar above the battery stand to the main bus bar (chandelier) shall be in accordance with Chapter 9.

Figure 3-1: Typical Arrangement of Cables for a Battery Stand

Figure 3-2: Minimum Dimensions for Bus Bar above Battery Stands

Battery suppliers shall provide a label or stamping on each battery containing the following information:

- Voltage

- The rating of the battery at a specific discharge rate, the temperature for that rating, and the end-Voltage to which the rating applies.

- The minimum and maximum Float Voltage

- The operating temperature at which the battery lifetime is guaranteed (e.g., 25 degrees C or 77 degrees F)

- The date of manufacture (may be part of the serial number), preferably in an easily intelligible format

Pilot cells (aka, the Temperature Reference cell) should be in the top tier of the battery stand and have the lowest Voltage reading after initial charge of all the batteries on that tier for that string.  Cells 1 and 24 cannot be used as the pilot cell.

For applications using VRLA batteries, there shall be a minimum of two strings.  This requirement is waived for small remote terminals and customer premise locations serving 96 or fewer POTS customers where space will not allow for the placement of two strings.  It is also waived for DSL backup.

All VRLA batteries shall have a minimum of 1/2” spacing between batteries to allow for natural circulation of air, and adequate top clearance (preferably at least 4”) to allow for maintenance.  The requirement for top clearance may be reduced to 1/2” for batteries whose posts/terminals are front-accessible, or when the batteries are in a slide-out tray so that the tops are accessible.

## 3.10	Battery Disconnects

A disconnect breaker or other means to disconnect the battery string (e.g., quick-disconnect plug) shall be connected in series with each string of VRLA batteries.  Battery disconnects may also be required by the Fire Marshal for flooded batteries.  The breaker or other disconnect shall be large enough to handle recharge capability.  When the Fire Marshall requires the installation of Battery Disconnects for each string of flooded batteries and/or an Emergency Power Off (EPO) switch, the EPO switch will disconnect the batteries, Engine, and AC Service.  This requires the installation of a battery disconnect with shunt-trip capability.

The Battery cabling must be sized on Voltage drop per Chapter 9.  The disconnect (and cable Ampacity when a disconnect is used) is sized at the 2 hour battery discharge rate (for an end point cell Voltage of 1.86 or 1.88 dependent on whether the application is Qwest Local or National Network] for lead-acid cells) multiplied by 125%.  The following table is an example of typical flooded battery sizes, their Ampere hour rating, and the recommended disconnect size.  This table represents the most common battery sizes used within Qwest.  The 2-hour rate sizing rule only applies to long duration (3 hour or more designed discharge times) battery applications.  For UPS type applications, the battery disconnect must be sized at a minimum of 125% of the expected maximum discharge current.

The following calculation examples apply to the table that follows (note that the table only applies generally to flooded batteries — for VRLAs or other sizes not listed, look up the 2-hour rate from the manufacturer documentation).

- Mini Tanks are rated at 927 Ampere-hours at the 2-hour rate, therefore 927A × 125% = 1158.75 Amperes.  That indicates the need for a 1200 Ampere battery disconnect.  Three 750 kcmil cables are the minimum number of cables required (the Ampacity of each 750 kcmil cable is 475 Amps).  This exceeds the minimum of four 350 kcmil cables required by Chapter 9.  Voltage Drop calculations (per Chapter 9) may require more cables.

- 1680 Amp-hr type batteries are rated at 415 Amperes at the 2-hour rate, therefore 415 × 125% = 519 Amperes, which indicates the need for a 600 Amp battery disconnect.  Two 350 kcmil cables are the minimum number of cables required (cable Ampacity of 350 kcmil cable is 310 Amps) based on this calculation, but Chapter 9 requires four 4/0 AWG cables or equivalent as a minimum.  Voltage Drop calculations (per Chapter 9) may require more cables.

.

Table 3-1 Typical Battery Disconnect Sizes for Flooded Cells

| Amphr Rating @ 1.75 V/cell | Amps @ 2 hour rate at 1.86 V/cell | Amps @ 4 hour rate at 1.86 V/cell | Amps @ 8 hour rate at 1.86 V/cell | 125 % of the 2 hour rate | Minimum Disconnect in Amperes |
| --- | --- | --- | --- | --- | --- |
| 180 | 49 | 31.9 | 19.5 | 61.23 | 70 |
| 520 | 127.1 | 87.4 | 55.8 | 158.89 | 175 |
| 840 | 208 | 140 | 91 | 260.00 | 300 |
| 1680 | 415 | 280 | 181 | 518.75 | 600 |
| 4000 | 927 | 653 | 418 | 1158.75 | 1200 |

There are a few possible scenarios that differ from the standard design already covered.

- •	Excess Rectifiers.  This scenario has the possibility of providing more current to the batteries than even the two-hour charge rate.  Obviously, this may operate the breakers, but excess rectifiers are the main cause of thermal runaway, and this is one of the reasons to place the breakers in series with the batteries.  The recommendation in these cases is not to upsize the breakers, but to shut off excess charging capacity.

- •	Excess Battery Capacity — Too Many Strings.  This scenario may actually help prevent thermal runaway by reducing the current going to each string on charge, even when there are excess rectifiers.

•	Excess Battery Capacity — Large Cells (Cells with large Amp-hour ratings require fewer strings).  Excess rectifiers coupled with this scenario could be a problem, because the large cells mean that fewer strings are necessary.  The worst case in this scenario is that the breaker sizing, based on the large Amp-hr rating of the cells, would exceed the total charging capacity of the plant.  For example, a 540 Amp-hour VRLA cell used in a 100 Ampere plant with three 50 Ampere rectifiers would call for a breaker rated at 200 Ampere.  However, the total charging capacity of the plant is only 150 Amp-hours.  Although the disconnect device will never trip on charging, it can still be useful as a maintenance tool for manually disconnecting the string.  In this case it may be necessary to lower the disconnect device rating (to 140 Amperes for example).  It might be wiser in these cases to not install a disconnect device.

CONTENTS

Chapter and Section 	Page

4.	Converters	 4-1

4.1	General	 4-1

4.2	Alarm Features	 4-1

4.3	Technical Requirements	 4-1

# 4.	Converters (DC/DC)

## 4.1	General

This unit covers DC/DC converters that transform the output of a rectifier/battery plant.  The converter output Voltage may be higher, lower, or at a different polarity than the input Voltage.  In some special cases, where ground, noise, or transient isolation is required, the output Voltage and polarity may be the same as the input.

Converters can be applied in two ways: as bulk converter plants or as imbedded (dedicated) converters.  Imbedded plants are generally provided as a component of the served equipment.  The requirements of this unit apply to bulk converter plants.

If the capacity of the converter plant is exceeded for any reason, the output Voltage of the converters must be lowered rather than allowing the plant to fail.

PLANT SIZING — The converter plant size is based on the peak current loads of the connected equipment.  A converter plant must not be designed to have short-term overload capability.  In other words, sufficient converter capacity must be provided for possible short-term peaks.

WORKING SPARE — The number of converters in a plant should be at least one more than is required for the total anticipated current drains defined above, so that the failure of any one converter does not overload the remaining converters.

## 4.2	Alarm Features

The following converter plant alarm indications are minimum alarming considerations (the alarms noted in the combined major and minor alarms may be broken out individually).  Alarms provided should include the ability to be wired to local audible and visual alarm systems as well as the remote alarm system.

- MINOR — One converter failed:  A single converter failure (as opposed to being turned off) will initiate a minor alarm.

- MAJOR — Converter major alarms include plant distribution or control fuse or breaker operation, low bus Voltage, high bus Voltage, and two or more converters failed.

## 4.3	Technical Requirements

Protection (fuses or circuit breakers) for feeds from a converter plant shall NOT exceed the capacity of the plant minus the spare converter.

Individual Converters should have individual power feeds, rather than a single power feed to the Converter Plant.  If there are feeds common to more than one converter, the combined total size of the converters served by the common feed becomes the “spare converter” size.

Converter output Voltage static regulation shall be ±1% over a load range of 10% to full load.

Converter input Voltage range shall be at least -42 to -59 VDC for nominal -48 Volt input, and (21 to (29.5 VDC for nominal (24 Volt input.

The converter case and/or shelf shall contain an adjustable high Voltage shutdown circuit that automatically shuts itself down when the output Voltage exceeds a preset value.  When this occurs,  a low Voltage alarm indication shall be given as a minimum.

The converter output Current shall be limited to no more than 110% of its rated capacity. The converter output Voltage shall be adjustable to ±10% of its normal output Voltage.

The converters plant shall have meters displaying the output Voltage and current.  Analog current meters shall have a scale with a range of 150% of the rated capacity.  The converters should have either a meter or LED bar graph to display the load current. They should also have test jacks to measure converter Voltage.

All components of the plant and converters shall be removable through front access.  The converter equipment shall be modular.  During growth and additions, the delivery of power to the using systems shall be maintained.

All converter equipment shall have a nameplate with a minimum of the supplier's name, model and serial numbers, input and output Voltages, and manufacturing date.

For loads with a different Voltage and/or polarity than the primary battery plant, two choices exist to serve them:

- Converter plant

- A separate Battery plant

For loads less than 100 Amperes, typically a converter plant is the preferred option.  For loads exceeding 100 Amperes, typically it is less costly over time to serve those loads with a new battery plant at their Voltage and polarity.  The engineer should evaluate the economics before making a decision.

Converters are considered separately derived DC power sources by Code.  This means that in addition to the frame grounding, the output return bus of the converter plant must be directly referenced to a COGB or OPGP (see Qwest Technical Publication 77355, Section 5.5).

CONTENTS

Chapter and Section 	Page

5.	Inverters (DC/AC)	 5-1

5.1	General	 5-1

5.2	Inverter Selection	 5-2

5.3	Load Classification	 5-2

5.4	Alarm Features	 5-2

5.5	Technical Requirements DC and AC Power Supplies	 5-2

# 5.	Inverters (DC/AC)

## 5.1	General

Inverters change DC to AC at a Voltage suited to the load, and although they are often truly uninterruptible, they are not classified as a commercial UPS.  Inverters are more reliable than a standard UPS and may be of the solid state or rotary type.

Two basic configurations are provided:

- Standby — in the standby configuration, the AC input powers the load directly and the inverter is a source of back up power.  This operating mode conserves the life of the inverter and conserves energy.  However, the incoming power is untreated so the load must be able to tolerate any power line disturbances that may be present.  This mode is also known as AC-preferred.

- ON LINE — in the on line configuration, the inverter operates continuously off the DC source to power the load, and the AC source, (if available) is the back up power.  The online option is preferable.  This mode is also known as DC-preferred.

Online is the preferred configuration.  An automatic static transfer switch is often provided to switch to commercial AC in case of an inverter failure.  A maintenance bypass switch must be provided.  The maintenance bypass and AC feed with its static transfer switch are not required in LNS when the inverter has redundant power modules that can carry 100% of the load (eliminating the need for maintenance bypass) during the service or replacement of a failed inverter module.

Components of the inverter shall be front-removable.

Inverters shall be modular to facilitate growth.  Maintainability shall be stressed in the design.  The design shall allow repair by module replacement.

Inverter nameplates shall contain the following information as a minimum: Supplier’s name, inverter model number, inverter serial number, and manufacturing date.

The following equipment should generally be connected to an inverter if it is found in a central office and uses AC power:

- Switches or other Network equipment that should have uninterrupted service and that require AC power.

- Computers essential to switch operation.  Typically, no more than 2 maintenance terminals need to be powered from inverter protected AC.  No printers or personal computers are permitted on the inverters.

- 911 equipment that is not DC powered.

- Fire Alarm panels.

- Card Entry Systems.

- Emergency/stumble/egress, or task lighting (this is an alternative to DC-powered lighting for these applications).

- Switch room telephone systems (key systems, wireless systems, etc).

- Outlets serving modems essential to network elements.

- Outlets serving devices installed in frames that control or are essential to the operation of equipment serving over 1400 DSO’s and/or any DS1’s or DS3’s (DISC controllers, TLS controllers, etc).

- The circuit shall be identified that it is inverter powered by a permanent label at the point of termination.

Uninterruptible AC power provided by an inverter is very expensive (due to the high cost of the inverter itself and the battery backup).  Non-critical and non-network loads should not generally be placed on the inverter.  The Common Systems Power Engineer and the Power Maintenance Engineer shall be the final arbiters if there is any disagreement over whether to place certain types of equipment on the inverter.

## 5.2	Inverter Selection

Inverter plants must be selected to have proper characteristics and designed to be compatible with the equipment served.

For inverters operating in a Stored Program Control System (SPCS) environment, all loads must meet the grounding requirements described in Chapters 4, 8, and 9 of Technical Publication 77355.

## 5.3	Load Classification

Inverter plants are always classified as an "essential load” for sizing the standby AC plant.  Inverters are also included as part of the "power failure load" for sizing the batteries of the DC plant that feeds them when the inverter is operated in the continuous "on line" mode.  Inverters must be included as part of the "busy hour" load for sizing the DC plant.

## 5.4	Alarm Features

The following alarm indications shall be provided for local and/or remote surveillance:

- Inverter "fail" — an inverter has failed.

- Inverter "supplying load" — a status indication used as an AC power failure indication for inverters normally operated in AC-preferred mode.

All points, loads, and alarms shall be accessible for connection to a Power System Monitor Controller (PSMC).  The inverter shall produce alarms as described herein and in Chapter 8.

Each fuse shall be provided with a blown fuse indicator connected to an alarm-indicating lamp on the control panel.

## 5.5	Technical Requirements

The inverter shall be capable of tolerating power factors as low as 0.8 (80%) leading or lagging without damage to the inverter.

Multi-phase inverters shall be able to operate with a line-to-line load imbalance of 20 percent or greater without damage to the inverter

All external metal parts shall be grounded, and the grounding requirements of Qwest Technical Publication 77355 shall be met.

The inverter shall have built-in protection against under Voltage, overcurrent, and over Voltage.

Inverters shall be capable of being mounted in 19" or 23" racks, or in a floor-mounted cabinet.

An n+1 inverter configuration should be considered for critical loads and in high profile offices.

Inverters are considered separately derived power sources and shall be equipped with a grounding bus, and a neutral bus on the output.  These busses should be grounded in accordance with Qwest Technical Publication 77355, Sections 5.5 and 4.2 (which follows NEC Code requirements for separately derived sources).

CONTENTS

Chapter and Section 	Page

6.	Uninterruptible Power Supplies (UPS)	6-1

6.1 	General	6-1

6.2 	Definition of Terms	6-1

6.3 	Technical Requirements	6-3

6.4 	Alarming and Control	6-5

# 6	Uninterruptible Power Supplies (UPS)

## 6.1	General

This unit outlines general engineering considerations for Uninterruptible Power Supplies (UPS).

UPS require cooling of the ambient air to allow for full output and longevity of components.  UPS equipment areas should be designed with the same environmental considerations as other equipment locations containing batteries.

The air in the room containing the UPS batteries must be exchanged a minimum of one complete change per hour to relieve the accumulation of battery fumes.  If the batteries are located in an enclosed cabinet, that cabinet must be ventilated to the outside room at a minimum of one complete air change per hour.  Local codes may require a higher rate of air exchange.

Larger UPS may induce extreme floor loading due to the combined weight of the system components.  The loading factor may require the engineering of special floors.  Some systems may require reinforced raised floors so that cool air can be introduced under the floor.

A UPS system must be engineered to be as reliable as the system it serves.  As such, the manufacturers’ recommendations for installation must be followed.  This unit is an engineering guide for UPS systems that are not so defined by the manufacturer and provide minimum requirements for all UPS systems.  Batteries for the UPS shall be flooded types wherever possible.  Isolation transformers shall be used on all UPS systems above 10 kVA.

All components of the UPS shall be removable via front access.

UPS shall be modular to help design growth.  Maintainability shall be stressed in the design.  The design shall allow modular replacement for repair as much as possible.  The design should be such that failure of any one module will not cause a complete UPS malfunction.

UPS nameplates shall contain the following information as a minimum:  Supplier’s name, UPS model number and serial number, kVA rating, nominal input and output Voltages, and manufacturing date.

## 6.2	Definition of Terms

UPS Definitions:

- AC LOAD PROTECTION — Devices to allow one of several loads to be isolated for fault clearance or maintenance.

- BATTERY BANK — a group of cells/monoblocs used to provide the required reserve power to the inverters while there is no AC input to the rectifiers.  The battery bank should be sized to provide the reserve for a minimum of 15 minutes.

- BATTERY DISCONNECTS — a means to open leads between the UPS and the battery bank.  This device should safely open both the + and - leads, as most systems are not grounded on either battery lead.  The device must be rated for the Voltage and current of the battery bank.  For DC battery strings having a Voltage greater than 250, disconnects are also usually placed mid-string to minimize technician risk during maintenance.

- BYPASS — a source of AC power (commercial AC or engine-alternator backup) that will replace the inverter output.  This source can be internal or external.

- HARD/MAINTENANCE BYPASS — an external source of AC that will allow shutdown of the UPS for maintenance and provide AC for distribution while the UPS power electronics components are not energized.

- DOUBLE-CONVERSION — This type of unit always converts AC power to DC, and then inverts it back to AC, providing truly uninterruptible and protected AC power to the load.

- FLYWHEEL — Some UPS systems (commonly known as rotary UPS systems) are equipped with a heavy flywheel (instead of battery backup) that provides 10-15 seconds of backup by storing rotational energy

- INVERTER — Unit that converts DC to the necessary AC Voltage required by the distribution system, normally 120/240 V single-phase, or 120/208 or 277/480 V three-phase.

- LINE-INTERACTIVE — This UPS unit normally passes a surge-protected commercial AC source through to the load, but switches to battery backup (through the inverter) in less than 4 milliseconds when the source is lost, or the quality of the AC waveform is poor.

- OFF-LINE — This UPS unit normally passes a surge-protected commercial AC source through to the load, but switches to battery backup (through the inverter) in less than 4 milliseconds when the source is lost.

- ON-LINE — (see the definition for double-conversion.)

- RECTIFIERS — change AC to DC to power the inverters and float charge the battery banks.

- ROTARY UPS — a UPS consisting of an electric motor coupled through a clutch to an alternator (sometimes incorrectly called a generator), and including a heavy flywheel to keep the alternator spinning for a short time period when commercial AC power is lost to the motor.

- STATIC TRANSFER SWITCH — a very-fast acting (typically less than 4 ms) automatic transfer switch that transfers a UPS (or -48 VDC powered inverter) from AC source to the DC backup or vice-versa.

- STATIC UPS — a traditional UPS consisting of power electronic components (in rectifiers and inverters), and DC backup (usually batteries).

- SUPER™/ULTRA™ CAPACITORS — may be used in a static UPS to provide very short duration (almost always 2 minutes or less, and typically 10-30 seconds) DC backup to feed the inverters.

- TRANSFER SWITCH — A means of transferring the distribution system from the inverter's output to an alternate source, usually commercial power, or a source that can be transferred to a standby generator.

## 6.3	Technical Requirements

Outlets served from UPS shall be labeled as to source.

CAUTION

High Voltage may be present on both the AC and DC sides of an UPS.  AC or DC Voltages may be as high as 540VDC and 480VAC.

AC wiring must be sized to meet manufacturers’ specifications.  Rigid conduit must be used in areas where activity could jeopardize the integrity of the system.

Four hundred Hz systems may require the use of line regulators to provide a match of impedance between the load and the UPS.

Breakers must be sized and coordinated with system components to ensure proper isolation of feeders due to faults or overloads.  The input and output main circuit breakers shall be equipped with a factory-installed shunt for UPS larger than 10 kVA.

DC wiring must be sized to meet manufacturers’ specifications for loop loss between the battery and the rectifier or inverter.  The Voltage drop must meet National Electric Code (NEC) requirements.  When the batteries are separate from the power electronics components of the UPS, the DC leads are usually run on cable racks or trays and should have RHW, RHH or XHHW type insulation.  Conduit may be used if both positive and negative leads are run in the same conduit.  Conduit may be used only if other means are not available due to space requirements.

The operating temperature of all AC and DC wiring in UPS equipment will not exceed 20 degrees F higher than the ambient room temperature or 46 degrees C (115 degrees F) whichever is higher.

Electrically operated disconnect devices (aka EPO switches) are required in some computer room installations by Code.  EPO switches/buttons should be guarded and preferably be pull-type rather than push-type.

The neutral lead of UPS systems must be grounded at one point only because it is a separately derived source when equipped with any transformer.  A dedicated transformer and switchgear are normally used to provide bypass power.  The neutral must be grounded at the secondary side of this transformer.  The ground lead must not be switched.  Grounding of computer areas served by UPS must be in accordance with the UPS manufacturers’ specifications and the requirements defined in Technical Publication 77355, Chapter 11 (the neutral and ACEG grounding of the output of the UPS in covered in Sections 4.2 and 5.5 of that same Pub).  Ground bonds between the UPS plant and the metallic structures shall consist of electrical conductors specifically provided for grounding purposes.  Incidental paths through framework, cable rack, building steel, etc., shall not be used for grounding purposes.  Daisy chaining between frames is not permitted.  The doors of the UPS enclosures shall be equipped with grounding strap connections for static electricity control.

The major power electronics components (and monoblock VRLA batteries) of UPS larger than 40 kVA shall be housed in freestanding, "dead front" vertical enclosures with a maximum height of 7 feet.  The enclosures may be mounted on heavy-duty casters with leveling screw jacks.  The enclosures shall be equipped with "piano-hinged" doors or equivalent.  These doors shall be equipped with locking mechanisms to prevent the doors from opening.  All sheet metal used in the enclosures shall be 16 gauge or better.  All joints and seams shall be welded.  Cable entry shall be through either the top or the bottom of the cabinet.

Forced air-cooling and/or ventilation are normally required.  Blower motors shall be equipped with sealed roller (ball) bearings.  Each enclosure with a blower for UPS larger than 40 kVA shall have a redundant blower.  A failure of a blower unit shall generate an alarm.  All air inlet and exhaust openings shall be protected with expanded metal guards.

UPS designed to serve non-linear loads shall have an output Voltage THD of less than 20%.  No single harmonic shall have an output distortion of less than 10% under any or all of the following conditions:  up to 100% non-linear load; up to 100% load current THD; and/or a load current crest factor up to 3.0.

The UPS shall have built-in protection against under Voltage, overcurrent, and over Voltage on both the input and output.

The UPS shall conform to NTA, Telcordia (Bellcore) TR-TSY-000757, Issue 1, Generic Requirements for Uninterruptible Power Systems.  The UPS shall also be Listed.

Wherever possible and feasible, flooded batteries specifically designed for high discharge rate applications will be used with UPS, rather than VRLA batteries.  When VRLA batteries are used, those designed specifically for high discharge rates (or general purpose batteries designed for many types of discharge rates) shall be used.

## 6.4	Alarming and Control

The UPS shall produce alarms as described herein and in Chapter 8.

Internal alarms and monitoring devices shall be built into the UPS to identify failed modules.

If the UPS utilizes a microprocessor and software for control, detection of a UPS unit failure shall be built into the software.  It is desirable that microprocessor-based units be equipped with an IP port for html and/or SNMP communication, or at least serial data communication through an RS-232 port.  Microprocessor driven UPS alarm/control will be either fully redundant, or capable of self-diagnostic and isolation in case of a microprocessor failure.  This isolation will remove the microprocessor control from the system, provide a dry contact alarm, and revert to conventional operation.

All UPS shall be equipped with dry contacts for connection to an alarm system; these contacts will provide indication of UPS unit failure and operating status.

Battery backup (separate from the batteries used for the primary backup of the loads fed from the inverter) may be provided within the UPS to maintain power to the internal clock or save microprocessor settings, in case of failure of the power source.  If such memory battery backup is provided, a low battery Voltage alarm shall be provided allowing sufficient time to permit battery replacement on a non-emergency basis.

CONTENTS

Chapter and Section 	Page

7.	Standby Engine-Alternators	7-1

7.1	General	7-1

7.2	Site AC Power Systems	7-3

7.3	Sizing and Ratings	7-4

7.4	Alternator Technical Requirements	7-5

7.5	Control Cabinet and Transfer System Requirements	7-6

7.6	Additional Engine Requirements	7-12

7.7	Voltage and Frequency Regulation	7-12

7.8	Additional Paralleling Requirements	7-14

7.9	Alarms and Shutdowns	7-15

7.10	Fuel and Lubrication Systems	7-18

7.11	Exhaust System Requirements	7-22

7.12	Starting Systems	7-23

7.13	Cold Starting Aids	7-23

7.14	Acoustic Noise	7-24

7.15	Cooling System	7-25

7.16	Safety	7-26

7.17	Hazardous Voltages	7-27

7.18	Portable Engines and Trailers	7-27

7.19	Portable Engine Connections	7-28

CONTENTS (Continued)

Figures	Page

7-1	30-Ampere Cable Hardwired to Single-Phase Engine-Alternator	7-33

7-2	30-Ampere Cable to Single-Phase Engine-Alternator Receptacle	7-33

7-3	100-Ampere Cable Hardwired to Single-Phase Engine-Alternator	7-34

7-4	100-Ampere Cable to Single-Phase Engine-Alternator Receptacle	7-34

7-5	100-Ampere Cable Hardwired to Three-Phase or Single/Three-Phase Engine-Alternator	7-35

7-6	100-Ampere Cable to Three-Phase or Single/Three-Phase Engine-Alternator Receptacle	7-35

7-7	200-Ampere Cable Hardwired to Single-Phase Engine-Alternator	7-36

7-8	200-Ampere Cable to Single-Phase Engine-Alternator Receptacle	7-36

7-9	200-Ampere Cable Hardwired to Three-Phase or Single/Three-Phase Engine-Alternator	7-37

7-10	200-Ampere Cable to Three-Phase or Single/Three-Phase Engine-Alternator Receptacle	7-37

# 7.	Standby Engine-Alternators

## 7.1	General

This unit contains requirements for all standby AC systems and equipment including engine-alternators with automatic transfer equipment to be deployed in all Qwest facilities.  Standby AC power plants provide long term backup for essential AC loads, as defined in Chapter 1 of this publication.

Terminology commonly used for AC power plants includes emergency, reserve, auxiliary, and standby.  Standby (as opposed to "Emergency") is used in this document in conformance with the definitions of Article 701 "Legally Required Standby Systems" and Article 702 "Optional Standby Systems" of the National Electric Code (NEC); as well as the definitions given in NFPA 37 and NFPA 110.  The use of the term emergency should be avoided because true emergency engines and their associated AC distribution systems have many additional maintenance and wiring requirements in the NEC.

The grounding system of a separately derived source (a few higher Voltage engine-alternators) shall be according to Technical Publication 77355 Chapter 4, and NEC Articles 250.30 and NEC 250.20D.  Grounding for most engines (those that aren’t separately derived sources) shall conform to Sections 4.8-4.10 of Tech Pub 77355, and Article 250 of the NEC.

All engine-alternators must conform to local code and should be coordinated with the local, state, or federal agency having jurisdiction.

Air dryers and/or compressors must not be installed in the engine rooms due to the static electricity and heat generated.

Qwest does not require n+1 for engine/alternators or transfer gear, although paralleled engines in an n+1 configuration should be considered for the most important facilities.

In some cases of load growth, if engine horsepower is sufficient to support a larger alternator, it may be less expensive to replace just the alternator rather than the entire engine-alternator set.  This might also be the case if the alternator fails.

Operating documentation (including control programming and prints/drawings) must be provided with each engine-alternator and transfer system.  The documentation should include how to start or shut down the engine; how to back out of a transfer operation; how to manually transfer the transfer system, and how to transfer the load when load shedding.  If this documentation can be shortened to a sheet or two for each operation, these sheets should be laminated and posted on the transfer and engine control cabinets.

Single-line diagrams for a site must be updated (and preferably laminated) by the electrical contractor whenever an engine or transfer system is added or replaced.

All systems and equipment to be deployed in telecommunication sites shall satisfy the relevant space and environment requirements of Telcordia (Bellcore) GR-63-CORE.  Major spatial (building space) requirements for standby AC plants are shown as follows:

- The clear ceiling height required for installation of an engine in a room shall not be less than 12 feet 6 inches.  This means the minimum height from the floor surface to the bottom of the lowest building structural.  Coordination may be necessary to ensure that the standby AC plant installation will not interfere with cabling, air ducts, or other building systems.

- The equipment weight, averaged over any 20 by 20 foot floor area, should not exceed an absolute limit of 140 pounds per square foot (140 lb/ft2) for equipment, supporting structures, cabling and lights, unless the floor has been certified by a building engineer to be able to support more weight.  Special building structural considerations may exist due to the load concentration and dynamic loads associated with the engine/alternators.  Professional Engineers contracted by the Qwest Real Estate Department can determine this, plus any earthquake bracing that must be done for the engine installation at the specific site location.

- All connections from the engine/alternator (e.g. exhaust, fuel lines, coolant lines, electrical, etc.) shall be made with a flexible section for control of vibration.

- The environmental requirements in Telcordia GR-63 and GR-1089 address temperature, humidity, heat dissipation, fire resistance, earthquake, office vibration, air borne contaminants, grounding, acoustical noise, illumination, electromagnetic compatibility, and electrostatic discharge.  Environmental test methods are included in these NEBS documents, and they may be used for evaluating equipment compliance with these requirements.

Qwest requires a factory representative to go to the job site for the initial start up of an engine-alternator.

The design engineering and installation of power systems for COs should conform to the requirements of Occupational Safety and Health Administration (OSHA) and all applicable local health and safety codes.  All power systems and equipment shall be designed and constructed to comply with applicable requirements of the NEC and with applicable local electrical and building codes.  When special requirements are necessary, they will be furnished by the Qwest Engineer.  The standby AC plant, as installed, shall also conform to the requirements of NFPA 37 (Standard for the Installation and Use of Stationary Combustion Engines and Gas Turbines), NFPA 110 (Standard for Emergency and Standby Power Systems), and the “Flammable and Combustible Liquids Code" (NFPA 30).

The documentation for standby AC plants shall be provided in a clear, concise, and organized manner per Qwest requirements.  The information shall include all the equipment building environmental requirements.

Engine-alternators should not be re-used in another site if they are over 30 years old.  Before they are re-used they should be looked at by a qualified diesel mechanic, either a Qwest employee, or an outside engine-alternator vendor.

## 7.2	Site AC Power Systems

A typical AC power system for a Central Office (CO) equipped with a standby engine-alternator consists of the following:

- Commercial AC Service Entrance

- Standby AC System

- Engine-alternator

- Transfer System

- Building AC Distribution System

Essential AC

- Non-Essential (may not exist in smaller buildings)

The main building AC disconnect should preferably be outside the engine room but relatively nearby.

For Qwest sites other than COs, AC requirements are defined in Chapter 11.

Commercial AC power is the normal energy source for most Qwest sites.  A prolonged commercial power failure requires backup in the form of standby AC power for both telecommunications services and essential building services.  The standby AC system consists of one or more engine driven alternator(s), transfer system(s), electrical and mechanical controls, fuel storage and supply system(s), combustion air intake and exhaust systems, engine starting system(s), and cooling systems appropriate to the type of equipment employed.

The size and type of standby AC system is determined by the combined building and equipment loads that require essential AC service.  Telecommunications equipment may represent only a portion of the total load.  The alternator kW should generally be sized between 125-333% of the essential load (see the next section for further detail).

## 7.3	Sizing and Ratings

Standby engine-alternator power plants are power-limited sources that can be overloaded by simultaneous starting of connected loads.

- In order to avoid transient overloads or oversizing of the engine plant, large motors (such as those found in chillers and other HVAC systems) should be on lead-lag control.  In addition, it might be necessary to add sequenced starting of rectification, although this need is rare.

Standby engine-alternators shall be designed and configured for reliable starting and continuous operation at full load within the range of operating conditions specified for Qwest sites.  Generally, the engines should be sized (based on the criteria below) between 125 and 333 percent of the existing peak load on the site (peak load will occur on battery recharge in the summer).  The more growth in load expected at the site over the next 10 years, the more the sizing would be towards the 333 percent.  When an engine is sized at greater than 333 percent of the existing peak, a load bank should be provided to prevent wet-stacking.  The system capacity specified shall be while operating under the following conditions:

  - Alternator output at the kW rating specified in the paragraph below.

  - Operating at the site specified altitude

  - Operating at the specified engine room ambient temperature

  - Maximum back pressure from the exhaust piping system

  - Maximum drop of radiator air handling system

  - Maximum pressure of fuel supply system imposed on the engine fuel pump.

  - De-rating for sites with high total harmonic content (Voltage THD > 15%).

The kW (kiloWatt) rating of all engines shall be based on the Continuous Duty Rating at an 80% power factor.  For small applications (under 30 kW where the power factor of the engine-alternator is 1.0), the engine-alternator must be capable of providing a peak load of 125% of the kW rating of the unit.

AC standby power systems shall provide outputs within Range A limits specified by ANSI document C84.1, "Voltage Ratings (60 Hz) for Electrical Power Systems and Equipment”, and provide one of the preferred systems Voltages per Table 1 of C84.1.

## 7.4	Alternator Technical Requirements

The alternator’s design and performance shall comply with National Electrical Manufacturers Association (NEMA) MG 1, Part 22.  The windings shall be "tropicalized" (i.e. designed to minimize effects of fungi and moisture).  Alternators shall also meet the following requirements:

- Insulation for the rotor and stator shall be Class H per NEMA MG 1, Section 1.65.  Design full load temperature rise shall not exceed the continuous duty values in NEMA MG 1, Section 22.40

- The engine-alternator shall be capable of continuously delivering the output (kW) specified by the Qwest Engineer for environmental ambient temperatures from –34 degrees C to 52 degrees C (-30 degrees F to +125 degrees F) and at the altitude where the engine-alternator is installed.  The manufacturer shall supply de-rating charts in one thousand (1000) foot increments.  This requirement shall be met at any power factor from 80% leading or lagging to unity, at any Voltage within the limits of ±10% of rated Voltage, and at a frequency of 60 Hz ±3 Hz.

- The alternator shall conform to the provisions of NEMA MG 1, Sections 22.41 and 22.45, "Maximum Momentary Overloads," and "Short Circuit Requirements", respectively.  Ground fault protection is required for sets with output Voltages greater than or equal to 480 VAC and/or output currents of 1000 Amperes or greater.

- The rotors (alternator and exciter) shall be in both mechanical and electrical balance at all speeds up to 125% of rated speed.

- The alternator bearings shall be the antifriction type.  The bearings, shaft, and housings shall be so designed as to prevent leaks onto the machine parts or windings.  Each bearing shall be sealed for life.

- The deviation factor of the alternator open circuit terminal Voltage shall not exceed 6%.  The deviation factor is determined in accordance IEEE Standard 115, “Test Procedures for Synchronous Machines”.

- The balanced line-to-line open circuit Voltage TIF (telephone influence factor) shall not exceed 50.  The line-to-line open circuit low frequency modulation is not to exceed 0.5 Volts peak-to-peak, in the frequency range of 5 to 30 Hz.  The total open circuit harmonic content of any line-to-line or line-to-neutral Voltage shall not exceed 3% rms, with no single harmonic exceeding 1.5%.

- The alternator leads shall terminate on the line side of the circuit breaker.  A means will be provided to prevent connectors from turning when mounted on breaker studs.

- Each engine-alternator set will be mounted on vibration isolators, either internal or external to the sets' skid base, as determined by the Qwest Engineer.

- Each exciter shall be of the brushless type, using a rotating rectifier bridge circuit.

  - Exciter field current shall be automatically controlled by the Voltage regulator.  The Voltage regulator shall provide under frequency protection.

- With the alternator stabilized at full load, the alternator shall be subjected to 150% of full load current for a minimum of five minutes.  Winding temperature shall be monitored during the test and shall not exceed the short-term temperature rise for the insulation.

- The output circuit breaker shall be equipped with adjustable instantaneous trips, long time trip elements (thermal trips), and a shunt trip circuit.

  - When an on-set breaker is required, the breaker assembly shall provide contact closure for OVERCURRENT audible, visual, and remote alarms.  Lockout contacts should be provided and interfaced with the control circuit to prevent starting of the engine before the breaker is reset.

  - The engine-alternator breaker trip settings shall protect the alternator from damage due to AC system faults, and avoid nuisance tripping.

- AC grounding will be in accordance with Qwest Technical Publications and the NEC.  The only acceptable method of grounding the neutral of a set producing 480 VAC power or less is to solidly connect it to the neutral of the commercial power at the house service entrance.

## 7.5	Control Cabinet and Transfer System Requirements

To minimize potential loose connections or trouble spots in the control circuitry, all interconnections of control circuitry wiring shall be stranded wire with crimp connectors and ring terminals securely fastened to terminating points with a machine screw (preferred).  Only one termination shall be provided per screw.

The only gauges that are to be physically located on a stationary engine are oil pressure, temperature, tachometer (if applicable), and fuel pressure non-electronic gauges.  These gauges must be remotable to the control cabinet.

The manufacturer shall provide a lighted unit control module for a stationary engine-alternator.  The control cabinet shall be a NEMA 1 enclosure with a hinged door.  Contents of the controller shall be solid state.  The solid state controller shall not be physically mounted on a stationary engine-alternator unless there is vibration isolation.

The engine-alternator set and/or control cabinet shall include the following:

- Gauges and Meters:

  - Oil Pressure

  - Coolant Temperature

  - Output Ammeter and Voltage Meter (equipped with a selector switch for each phase)

  - Running Time Meter

  - Frequency Meter

- Manual Selector Switch with positions for:

- RUN or MANUAL operation

- STOP or OFF

- REMOTE or AUTOMATIC operation

- Others:

- Remote, 2-Wire control start-stop terminals

- Manual reset Field Circuit Breaker

- Indicator lamp(s) for the alarm conditions causing an automatic engine shut down.

- An alarm-reset switch shall be provided to clear the indicator lamps and reset the system to allow restarting of the engine after an alarm shutdown.  The control design shall be such that the alarm must be reset manually (either on the engine or from a remote location).

- Manual reset Exciter Field Circuit Breaker.

- Emergency STOP switch.

- Dry alarm contacts for each failure condition.

- a Locking screwdriver type potentiometer shall be provided to adjust the following:

- Voltage (5%)

- Frequency (2%)

The remote control cabinet shall meet the requirements of this document.  All connections between the remote control cabinet and the set cabinet will be run in conduit.  These leads may be run along with the alarm leads.

The cabinet shall be front access via a hinged door that will latch.  All switches, lamps, gauges, and meters shall be mounted on the door.  All electrical wiring shall be routed and secured to prevent connection deterioration due to movement and to allow access to the cabinet interior.

For floor mounted cabinets, leveling screws, wedges, or shims shall be part of the usable cabinet to level and plumb the cabinet and to compensate for variations in floor flatness.  In addition, there shall be four holes provided in the corners at the bottom of the cabinet that will allow 5/8-inch anchor bolts to secure the cabinet to the floor.  The cabinet shall have a kick plate extending a minimum of 4-½ inches from the floor.

All Automatic Transfer Systems shall be listed to Underwriters Laboratory (UL) 1008 or 1066 (restricted and certified are not acceptable), and meet the requirements of NEMA ICS 10, Part 1 Standard, and ANSI C37.16 as applicable.  The transfer system should be sized to the main entrance facility whenever possible.

The transfer system itself shall be able to withstand 100% of its closing ratings.

Each automatic transfer system can be either an electrical or solenoid operated mechanism.  The transfer system should be either circuit breakers or a switch.  If breakers are used, these breakers may be used as the ground fault current protection device (when that is required for larger systems and/or higher Voltages).  Where permitted by local Code, the commercial breaker may also serve as the main service breaker.  External shunt trips with engine start inhibit may be provided if required by local fire codes.

Circuit breakers shall be of the thermal-magnetic type, rated for the fault current, and must be Listed.  Contacts shall not be able to be held closed during an overcurrent condition by holding the lever in the closed position.  They shall be a trip-free type.  The AC circuit breakers shall be clearly marked as AC breakers (not DC).  AC Circuit breakers shall generate an alarm signal when they either are in the tripped state or turned off.

The transfer system and its devices shall meet all requirements of the applicable UL and ANSI standards and be rated for fault current.  Ferrous materials shall not be used for current-carrying parts.

All transfer systems shall be equipped with plug-in, draw-out type elements, or a maintenance bypass isolation switch to facilitate maintenance and replacement (such as the inspection and replacement of main arcing contacts) without creating an extensive power outage.

Automatic transfer systems can be either equipped with a load disconnect delay option (preferred) or closed transition switching (not recommended for COs).  The disconnect delay option shall be set for a 3-7 second delay.

The manufacturer shall supply interconnection information for connecting the engine-alternator with an Automatic Transfer System.  A manufacturer’s representative shall review all installed new transfer systems to ensure they are properly installed and working.

There shall be a single standby engine-alternator test switch mounted on the AC switch gear.  This test switch will simulate a Commercial AC failure to the standby engine-alternator and all transfer systems.  Operating this Test switch will cause all of the standby engine-alternators to start, and all transfer systems that operate when there is an actual AC failure to transfer.  Restoring this test switch will cause the standby engines and transfer systems to proceed with their normal timing to return to Commercial AC and engine shut down.

For all automatic transfer, the system shall be capable of the following:

- Recognize the occurrence of a power failure.

- Open the commercial power source.

- Start the engine-alternator set.

- Close the alternator circuit breaker.

- Automatically control loading of the emergency bus.

- Recognize the return of commercial power.

- Transfer all loads from the standby power source to the commercial power source (only if the commercial AC load has been restored for 30 minutes).

- Shut down the engine-alternator.

There shall be a time delay for engine start, a time delay on retransfer to permit polyphase motor stop, a time delay on shutdown to permit engine cool down, and a time delay before transfer to engine to permit warm-up, polyphase motor stop or sequential loading.  There shall be a minimum run time.  All of the above times will be per engine manufacturer’s specification.

For automatic paralleling of multiple engines, the system shall be capable of performing the following operations:

- Recognize the occurrence of a power failure.

- Open the commercial power source.

- Initiate the Start signal to all engines simultaneously.

- The first engine to reach proper Voltage and frequency closes its on-set breaker initiating closure of the engine transfer breaker powering the static loads;

- As additional engine-alternators are paralleled to the essential bus, the Load Management Controller connects these loads on a priority basis.

- Recognize the return of commercial power.

- Transfer all loads from the standby power source to the commercial power source after the Holdover Timer has operated.

- Shut down the engine-alternator.

There shall be engine-starting contacts that will allow each unit to be started independently.

For automatic paralleling of the engines to the commercial grid system, the ATS shall be capable of performing the following operations:

- Initiate the Start signal to engine;

- Bring the engine up to speed;

- Synchronize and parallel it with the utility;

- Gradually transfer all loads from the commercial source to the standby source;

- Open the commercial power source;

- Upon completion the controls shall synchronize and parallel it with the utility;

- Then it shall gradually reduce the load on the standby source to zero;

- Then it shall open the standby source connection;

- Shut down the engine-alternator.

Note: 	Utility company permission must be obtained to allow paralleling to the commercial grid with the Qwest engine/alternator.  Special protection mechanisms may be required by the utility to ensure that the engine-alternator will not export power onto their grid when they want it de-energized for maintenance.  The paralleling of the two power sources increases the short circuit current magnitude on the building distribution system.  The engineer must consider this when specifying the short circuit interrupting rate of the distribution system protective devices.

The standby AC plant shall be equipped with load management features.  Both manual and automatic control capabilities shall be provided for sequential operation of the served load.  The system shall provide suitable time delays to prevent failure of the standby plant in response to transient conditions.

The system shall be equipped with a test switch to facilitate manual simulation of a power failure.  The system shall be equipped with a manually controlled retransfer override.  The system shall be equipped with indicating lights to indicate the source feeding the load.

Each automatic transfer system shall include a control panel.  The transfer system should preferably be outside the engine room (but relatively nearby).  An isolation plug in the wiring harness shall be provided to disconnect all circuits between the control panel and the main transfer panel.

Full phase Voltage sensing must be provided.  Full phase protection shall also be provided.  Three-phase relays may be field adjustable, close-differential type, with 92-95% pickup, and 82-85% dropout.  Relays are to be connected across the commercial AC Voltage input line side of the transfer system.

Independent Voltage and frequency sensing of the commercial source must be factory preset to initiate transition to standby at 90% Voltage and 58 Hz.

Exercise timers must be provided.  They must be adjustable for one week, two weeks, or monthly operation.

Synchronization for paralleling (whether to the bus or the grid) must occur within 20 electrical degrees.

The neutral shall not switch except on sets where the output Voltage exceeds 600 VAC.  The neutral and ground shall not be bonded at the transfer system, although they may be bonded at a very close panel in small sites.

Meters may be either analog or digital.

The overcurrent protection device can be either a fuse or a circuit breaker placed in the ungrounded supply lead.

All components must be marked on both the schematic drawings and in the cabinets themselves.

For nominal 208 VAC systems of greater than 1500 Amps, or nominal 480 V systems of greater than 700 A; upon loss of a single-phase (for more than 10 seconds) from either commercial or engine-alternator source, the transfer system should lock out the respective source and issue an alarm.  The transfer system may be set up to automatically allow reconnection if the lost phase returns for 10 seconds or more; or it may be set up to require manual intervention.  This single-phase lockout prevention is allowable for smaller systems as well.  The system may be powered from the engine start-control batteries or from an AC inverter source.

## 7.6	Additional Engine Requirements

Engines must be "In-Line" or "Vee" types, water cooled, and mounted on a common steel sub-base.  The engine is to be shipped with required accessories (except those items subject to damage in shipment).  All parts in the engine shall be new.  Engines should have replaceable cylinder liners.

All engine-moving parts must be maintainable.  Any "lifetime" - permanently lubricated parts must be easily replaceable and 100% warranteed for material and labor for a minimum of 7 years from the date of installation.

## 7.7	Voltage and Frequency Regulation

The Voltage regulator shall be of the solid state design and shall not be frequency-sensitive between frequencies of 55 to 67 Hz.  The regulator shall sense all phases.

On engine-alternator sets equipped for parallel operation, the regulator circuit shall have adjustable cross current compensation.  The Voltage droops due to the cross current compensation circuitry shall be adjustable from 0 to 5% of the set's rated Voltage and shall be factory set at 3.5 to 4%.

The Voltage regulator shall be furnished with an adjusting rheostat that should allow the alternator terminal Voltage to be adjusted ±10% of its normal value.  Means for Voltage adjustment shall be furnished at the control cabinet.

With the Voltage regulator operating, the cross current compensation shorted out, and the thermal effect constant, the regulator shall control the terminal Voltage at any load from 0-100%, and from 0.8 leading or lagging to 1.0 power factor.  This terminal Voltage shall be within 2% of nominal when the no load speed is as much as 3 Hz above 60 Hz.

With the Voltage regulator operating, the regulator shall hold the alternator output terminal Voltage constant within 2% over an environmental ambient temperature range from --30 degrees F to 125 degrees F, with a speed change of ±5%, based on the following conditions:

- The cross current compensation is shorted out.

- The load power factor is between 80% leading or lagging and unity.

- The engine has stabilized at its operating speed.

- The governor is adjusted for any droop between 0 and 5%.

- The ambient temperature remains within a 30-degree band after 5 minutes of operation.

Each alternator, exciter, and Voltage regulator assembly should have under frequency and over Voltage protection, including those conditions associated with shutdown and/or coast down.

When load on an engine-alternator is increased in 25% steps from 0-25%, 25-50%, 50-75%, and 75-100%, the output Voltage should recover to within 0.5% rms of the previous Voltage within one (1) second after reaching the new load.

When the full-rated kVA load is rejected in one step, the transient surge Voltage shall not exceed 20% of the rated Voltage and shall recover to within 1% of the new steady-state Voltage within two (2) seconds.

Either a hydraulic or an electronic governor that meets the following requirements can be used.  Isochronous type governors are preferred, with the engine-alternator set manufacturer to specify the type used.

- The governing system shall be capable of providing frequency vs. load regulation characteristics from isochronous to 5% droop.

- There shall be no sustained periodic variations in alternator output frequency under any conditions, including abrupt load changes.

At any constant load from no load to full load, the maximum frequency ripple for the AC output shall be 0.15 Hz (¼%) at any frequency between 57 and 63 Hz and at any load from no load to full load.  This requirement is intended to apply at steady state conditions including stable temperature within the governing system.  Frequency variations within the 0.15 Hz range shall be random (aperiodic).

Frequency drift due to changes in governing system temperature shall not exceed ±0.15 Hz for steady state operation at any load from no load to full load.

Note:	"Steady State", for the purposes of this requirement is defined as operating at constant real (kW) load for a minimum of 5 minutes after full speed is attained at start up, or, for a minimum of 2 minutes after the disappearance of transients in output Voltage and frequency due to a load change.

After stabilizing at steady full load conditions, the engine-alternator set shall return to the same output frequency ±0.15 Hz when load is repeatedly added or removed.  This requirement shall be met for isochronous and droop operation, where applicable.

The output frequency shall be adjustable over the range of 57 to 63 Hz from the system control cabinet.  External droop adjustment shall be provided at the governor or, where droop adjustment is via electrical means, by means of a potentiometer located within the engine control cabinets.

For both increasing and decreasing loads, the change of alternator output frequency with load shall be within 1/4% of true linear response with the governor set for any droop between 0 to 4%.

The response of the engine-alternator set to sudden changes in load shall meet the following criteria:

- For any sudden quarter-load change from no load to full load (increasing or decreasing the load) the frequency shall recover to and stay within the 0.15 Hz band within one second.

- For any sudden full load change (full load to no load), the frequency shall recover to and stay within 0.15 Hz band within 2.5 seconds.

- For any sudden quarter-load change from no load to full load (increasing or decreasing the load) the frequency shall depart from the steady state value by no more than 2% of the steady state value.

- For any sudden full load to no load change, the frequency shall depart from the steady state value by no more than 5% of the steady state value.

- For all of the above, the frequency shall stabilize at the steady state value after no more than one overshoot and no more than one undershoot.

Hydraulic governor mechanisms, where used, shall be designed to employ the same oil used in the engine.

## 7.8	Additional Paralleling Requirements

For engine-alternator sets equipped for parallel operation, the Voltage regulator and governor circuitry shall be designed to allow droop compensation type paralleling.  Standby engine-alternator sets equipped for automatic paralleling shall also be provided with means for manual synchronization (e.g., phase lamps, sync scopes, etc.).  For paralleling applications, the engine-alternator breaker will be of the size and type to ensure protection of the engine-alternator in case of out-of-phase paralleling.

Each alternator set equipped for parallel operation shall have suitable characteristics to permit it to be paralleled with another unit or units specified by the Qwest Engineer.  Each set shall be capable of operating in parallel with the set(s) so specified at any load from no load to full load, at any power factor from 1.0 to 0.8 lagging, while meeting the following requirements:

- Circulating current shall not exceed 10% of the combined full load current of all sets in parallel.

- The transfer of power between sets shall not exceed 2% of the rating of one set, and such transfer shall not be cyclic.

- The division of real load between sets shall be proportional to the set capacity.

For automatic paralleling, the system shall also be capable of paralleling the alternators and sending signals to automatically close successive load group circuit breakers as each associated alternator is brought on-line (or the load can be transferred all at once, if not too large, when all sets are paralleled);

Recognize the non-operation of any alternator(s) and open the designated load circuit breakers to shed/disconnect those loads to maintain system operation if there is not sufficient capacity to support all of the loads.

## 7.9	Alarms and Shutdowns

Standby AC plants must be capable of extended operation without the intervention of an operator.  Computer-based operating systems have been developed for remote surveillance of alarms.  The standby AC plants covered by these requirements shall provide alarm interfaces with maintenance and operation systems in accordance with requirements in this publication.

An alarm termination strip shall be provided for all the engine alarms.  The engine installer shall run the alarms from the engine to the terminal strip.  The terminal strip(s) should normally be in an EAT (Engine Alarm Termination) box located in the power room or engine room.  The installer will be required to label the engine alarms and analog monitoring points on the terminal strip(s).  Engine alarms and analog monitoring points are covered in this chapter and in Chapter 8.  The alarms and analog points are run from the EAT box to the PSMC by a Qwest-hired subcontractor familiar with PSMC installation and programming.

Normal shutdown of standby AC plants operating under manual control shall be accomplished by depressing a "STOP" or "OFF" switch located on the plant control panel.  It shall be placed in a convenient location, readily accessible and clearly marked.

A momentary contact push button type switch designated "EMERGENCY STOP" shall be provided on each control panel or cabinet.  When this switch is actuated, the set shall shut down and an alarm indication shall be given.  The "EMERGENCY STOP" switch function shall also be capable of being duplicated by a switch located as required by local code (generally outside the engine room or enclosure door).  The button/switch shall be in a housing, or otherwise protected, to prevent accidental operation.

There must be a manually controlled shutdown device mounted on the engine.  Operating this device shall:

  - Shut down the engine;

  - Close a solenoid-operated valve in the fuel line;

- Activate alarm circuits; and

- Disable the set's starting circuits

Operating conditions to be monitored for standby AC plants include those listed below.  Where an engine-alternator set employs additional features or support systems essential to proper operation of the plant, additional monitoring and/or alarms may be required.  Visual alarm and status indication shall be provided by colored lamps mounted directly on the local and, where present, remote control cabinet.  Provisions shall also be made for transmitting alarm signals per the alarm requirements in this publication.

- The local control cabinet shall also be equipped with meters or gauges, with minimum accuracy as indicated below in parentheses, providing the following outputs:

  - Alternator Output (alternator output meter shall be duplicated on the remote control cabinet, where equipped);

    - Amperes (3.0%)

    - Volts (3.0%)  (Engine and Commercial)

    - Frequency (1.0%)

    - Kilowatts (2.0%)

    - Lubricating Oil Pressure (5%)

    - Fuel Pressure (5%)

    - Lubricating Oil Temperature (5%)  (over 900 kW)

    - Engine Temperature (3%)

    - Hours of Operation (0.1 hour)

    - Tachometer

  - Engine Start Battery Voltage (Operational at all times, not just during engine run)

- The control cabinet and/or transfer system should be equipped with step-down current and Voltage transformers to meet the monitoring needs of the Power System Monitor Controller at the site (these are most often only in the transfer system on the load side, or in a subsequent load side cabinet).

An alarm indication shall be given and the plant controls shall shut down affected standby engine-alternator sets if one or more of the conditions listed below exist.  For each of the conditions listed in this section, the engine-alternator set shall shut down and require a manual reset after the problem has been cleared in order to restart the set.

- Low Engine Oil Pressure— operates if the oil pressure falls below the safe value recommended by the manufacturer

- Engine Over Crank — operates if the engine does not come up to a threshold speed within 10 seconds after three cranking attempts

- Engine Over Speed — operates when engine rpm exceeds 108% of normal operating speed

- Over Voltage or Under Frequency — operates if the alternator Voltage exceeds the normal operating range by 15% to 18% and/or the frequency deviation is greater than 3 cycles for 5 cycles (the engine should shut down on an inverse time delay basis)

- Over Current — operates if the alternator circuit breaker trips open

- Reverse Power — (required only for engine-alternator sets equipped for parallel operation, which may include paralleling with the commercial power) operates if the engine-alternator receives reverse power in excess of the threshold value specified by the manufacturer

- Differential Fault — (required only for engine-alternator sets rated 800 kW or larger and when the engine output breaker is less than 50% of the transfer system breaker) on sets so equipped, operates if the differential fault relays are energized due to differential fault current

- Ground Fault — (required only for engine-alternator sets with output Voltages greater than or equal to 480 VAC and/or sets with rated output current of 1000 Amperes or greater) on sets so equipped, operates if the ground fault protection device is activated

- Control Breaker or Fuse — operates if a circuit breaker or fuse providing power to essential engine-alternator set control functions operates

- High Coolant Temperature — operates if the temperature of the coolant, measured on the engine side of the set mounted thermostat, exceeds recommended coolant temperature by 15% (sensing arrangements shall be such that a shutdown signal will be issued if loss of coolant occurs)

An alarm indication shall also be given if one or more of the following conditions exist.  These conditions indicate impending problems, which may result in plant shutdown or other impairment if corrective action is not taken.

- Charger Failure — an Alarm shall be issued if the charger(s) floating the start/control batteries fail (or have high or low Voltage)

- Fuel System Trouble — for plants equipped with auxiliary fuel pumping systems and/or day tanks, an alarm shall be issued if the fuel level in the day tank is above or below the normal range

- Preliminary High Coolant Temperature — an alarm may be issued if coolant temperature in a liquid cooled diesel engine rises to within 10 degrees F of the "High Coolant Temperature" shutdown point (although this alarm may be available, it might not be wired past the EAT box, depending on the spare points available on the PSMC)

- Low Coolant Temperature and/or Block Heater Failure — an alarm shall be issued if the heating element fails or if coolant temperature drops to a level that may impair starting reliability

- Visual Alarm Codes — Visual alarm and status indications are defined in Chapter 1 except as noted.

Note: A red indicator on a circuit breaker indicates closed and is not an alarmed condition — per the NEC.

## 7.10	Fuel and Lubrication Systems

The rate of fuel supply to the engine's injection system shall be as required to prevent stalling, over speed, or over temperature under any steady state or transient loading conditions within the engine-alternator set's rating, and when operating within the environmental limits (temperature, altitude, and humidity) as stated in Telcordia GR-63.

Manufacturers shall provide fuel consumption charts for their systems operating at full, ¾, and ½ loads.

Acceptable fuels for use that should be considered are diesel, natural gas, propane, and gasoline.  Diesel engines shall be capable of operation with No. 2-D, or winter blend (combination of #1 and #2 diesel) fuel per ASTM Specification D-975.  Natural gas engines should be backed up by a propane source.

Note:  In special environments governed by special governmental rules (National Forest, National Parks, wilderness, etc.) the fuel used will be based on regulatory requirements.

The fuel tank will be installed in a location as near as possible to the engine-alternator in accordance with Code restrictions.  Because the fuel pump influences fuel tank location, the manufacturer shall provide fuel pump lift data.  Fuel tanks shall be installed per Code and Qwest policy.  The use of double wall tanks with a cavity leak detection system is preferred (double-walled tanks are required for all direct-buried tanks.  All single-walled tanks must have a containment structure — vault, curb, etc.).

Fuel tanks should be sized at a minimum of 36 hours of reserve based on full engine load.  Depending on how hard the site is to access in the winter, tanks with much greater reserve may be decided upon by the Common Systems and Power Maintenance Engineers.  The fuel consumption is given by the engine manufacturer.  However, if it cannot be found, it can be estimated as 0.07 gal/kW/hr at full load for diesel fuel and 0.1 gal/kW/hr for gasoline and LPG (propane) engines at sizes 50 kW and larger.  For smaller sizes, estimate use at 0.1 gal/kW/hr for diesel engines and 0.14 gal/kW/hr for gasoline and propane.  Note that generally, diesel and gasoline fuel tanks should not be filled to more than 95%; and propane tanks should generally not be filled to greater than 85% (especially at altitude).

A day tank is a fuel transfer tank used when the engine’s fuel pump does not have the necessary lift to draw fuel from the supply tank or there is excessive back pressure on the return line due to the fuel tank being mounted above the engine.  The day tank pump (and all other fuel pumps) shall be a DC driven motor for pumping from the storage tank.

DAY TANKS SHALL BE AVOIDED WHENEVER POSSIBLE (by use of a high-lift fuel pump when the required fuel lift is between 6-18 feet — note that if the lift is less than that, no day tank or high-lift pump is required:  the standard on-set engine pump can do the job).

If the use of a day tank is unavoidable, it shall incorporate both a containment device and a leak detection alarm.  In addition, it should be equipped with a high fuel level and a low fuel level alarm.  It should be equipped with a return line to the main fuel tank and a vent that is routed outside of the building.  It should be sized to provide a minimum of 1 hour engine run at full load.

Base fuel tanks under the engine are allowable, but when used, if they elevate replaceable engine components to more than 7 feet off the floor or ground, a catwalk must be provided.

When a day tank or high lift fuel pump is not used, and the tank is not above the engine, the return line should extend at least halfway down into the main tank (so that it is normally submersed) to prevent air getting into the fuel system due to backflow.  The return point in the tank should be spatially far away from the feed line pickup.

Fuel tanks shall be monitored in accordance with EPA, State, Local, and Qwest requirements.  Contact the local Qwest Environmental Consultant and/or CSPEC Engineer and/or Real Estate Engineer for approved monitoring systems.  At a bare minimum, fuel tanks must have a low fuel alarm.  All direct-buried tanks and any above-ground or vaulted underground tanks where the total site fuel storage is equal to or greater than 1320 gallons must also have an overfill alarm, and a monitoring system capable of at least monthly leak detection tests, including the interstitial space between the two tank walls.

Fuel tank monitors shall be equipped with a dialup modem and a working phone line (some sites were phone service is inaccessible may be exempt from this requirement).

Fuel delivery and return systems shall meet all national, state, and local codes, and applicable components shall be Listed.  When rigid piping is used, it must be black iron, and flexible sections or aeroquip hose in containment shall be placed between the engine and the supply and return lines.  A site window/glass shall be provided in the feed fuel line.  A solenoid-operated valve (powered from the engine start/control batteries) in the fuel line feed shall be provided for and connected to the emergency stop switch (to close when the switch/button is pressed/activated or the wiring is cut or burnt through).  There should be a normally closed manual bypass around this valve.  It is preferable that this valve be at the highest point in the line between the main tank (it may even be located on top of the tank) and the engine, or at least at a point above the engine fuel pump if possible.  If the placement is outdoors, the solenoid valve should be enclosed in a rain-resistant opaque enclosure.  For sites where the main tank is located above the engine pump, the solenoid valve must be located between the main tank and the first point of entrance into the engine room/enclosure (it may be placed right after it enters the room/enclosure).

When main fuel tanks are located above the engine or day tank they serve they shall have an anti-siphon valve in the feed line at the point they enter the engine room.

In some jurisdictions, fire marshals may require a valve (in the feed line) that closes when there is a fire in the engine room/enclosure.  This valve contains a meltable link that closes the valve when the temperature reaches approximately 195 degrees in the room/enclosure.

Grounding of fuel tanks shall conform to Qwest Technical Publication 77355, Chapter 4.  In addition, copper and galvanized piping shall not be used in fuel systems because of the impurities they may introduce into the fuel injectors.

The primary and secondary fuel filters and strainers shall be of the replaceable element type and of sufficient capacity to permit a minimum of 200 hours of continuous operation without requiring service.

Note:	This requirement will also be met when operating with fuels containing total organic and inorganic particulate matter (i.e., 1 micron or larger) of up to 5 milligrams per 100 cubic centimeters of fuel.  For example, if the engine filtration system(s) removes 100% of the particles 1 micron or larger, the filter or combination of filters shall be sized to trap and hold approximately one pound of particulate matter for every 2000 gallons of fuel circulated through the filters.

Diesel fuel systems will be equipped with water separators.

The fuel control system shall not require lubrication, adjustment, or other maintenance more often than every 500 operating hours.

A manually-operated, DC electrical or mechanical, permanently-mounted priming pump shall be incorporated in the on-set fuel system.  The priming system shall be capable of priming the complete on-set fuel system, starting with drained fuel lines to the supply tank and a drained on set fuel system, in 1 minute or less.

When a high lift fuel pump is used, it shall be capable of delivering at least 120% of the set's Fuel consumption rate when the set is operating at full-rated load and the suction lift (including flow losses in pipe and fittings) is 15 vertical feet of diesel fuel.

The fuel system shall consist of two supply and return loops:

- Fuel from the day tank or fuel supply tank flows through a fuel strainer, a gear or belt-driven fuel pump, and possibly into a fuel cup (the fuel cup is only found on engines with a high lift pump).  A return line provides a path for fuel not consumed by the engine to return to the day or fuel supply tank.  This return line shall normally be free from traps and/or valves (a check valve may be used in the rare cases where the tank and/or a significant portion of the return line is above the engine), and shall be at least as large as the supply line.

- The second loop runs from the fuel cup (on those engines with a fuel cup) to the engine's fuel metering/injection system (usually filtered and boosted by a high-pressure fuel transfer pump) with unburned fuel returning to the fuel cup (or to the day or main tank in the absence of a high lift pump).

Filter elements in the engine lubrication system shall be adequately sized to permit a minimum of 168 hours of continuous operation without replacement of the elements.  The lubricating oil capacity of the set shall also be adequately sized to enable unattended operation for a minimum of 168 hours.

Positive lubrication shall be provided for all moving parts in the engine and accessory drive.  The lubricating oil pump shall be gear-driven from the engine.

Lubricating oil filtration shall be of the full-flow type.  The lubricating oil filter shall have a built-in bypass arranged to permit oil to bypass the filter if the filter element becomes clogged.  Lubricating oil filters shall be of the replaceable element type.

If the lubricating system is designed to require priming after the system is drained for any reason, a manually operated pump shall be provided.  This pump shall be permanently mounted on the engine-alternator set.

Lubricating oil vapors shall not be vented within the CO building unless the engine room only ventilates to the outside.  All lubricating oil vapors from the engine should be recycled or consumed within the engine.

A lube oil pressure switch/gauge equipped with pressure sensors shall be provided to operate appropriate electrical contacts to shut down the engine if lubricating oil pressure falls below a safe level.

## 7.11	Exhaust System Requirements

The engine exhaust manifold provides the channeling for exhaust gases from each cylinder to an exhaust outlet.  The manifold shall afford a minimum of backpressure and turbulence to the engine cylinders and valves.  The two primary types of manifolds are the dry air-cooled and the water jacket water-cooled.  Air-cooled is preferred.

Exhaust pipes must comply with applicable codes.  The minimum requirements are as follows:

- Pipes shall be wrought iron or steel and strong enough to withstand the service.

- Pipes must not be supported by the engine or silencer.

- Pipes must use vibration proof flexible connectors.

- Pipes must have a clearance of at least 9 inches from combustible materials and terminate outside the building.

- Pipes in an engine room or walk-in enclosure (does not apply to external enclosures that are not walk-in) must be guarded and/or insulated to prevent burn injuries to personnel and excessive heat in the engine room.  For personnel protection, the guards or insulation is not required to extend above 7 feet high.  Insulation used solely to prevent heat buildup is at the discretion of the designer of the system.

- All connections shall be bolted flanges with gaskets, or welded.  No automotive type exhaust pipe clamps are permitted.

- The outlet of the exhaust pipe should be a 90 degree horizontal bend, designed for minimum back pressure, with the end of the pipe cut at a 45 degree angle, scarfed, with expanded metal over the open end.  For cases where the outlet must be vertical (to meet air quality rules, or prevent backflow of the exhaust into the intake, etc.), caps and or bird screens should be used to prevent intrusion of water or debris, but hinged rain caps are not permitted due to their propensity to rust shut (unless they are made of aluminum or stainless steel).

A piece of flexible, bellows-type exhaust pipe must be used between the engine exhaust connection and the exhaust piping system.

Exhaust silencer(s) shall be provided for each engine, sized per engine manufacturer recommendations, and engineered for a sound level specific to the site.

Exhaust must extend above the building whenever possible, and not be placed near fresh air intakes for the building.  Exhaust must meet local, state, and federal laws and requirements.

## 7.12	Starting Systems

The battery shall be sized to permit a minimum of five (5) cranking attempts of 30 seconds duration at the design low engine room temperature specified by Qwest (40 degrees F).  After the third cranking attempt, no more attempts to start the engine should be made, and the control cabinet should issue an alarm  labeled "overcrank".

The start and control batteries shall be Ni-Cd or Lead Acid type.  The batteries shall be covered with protection while working on the engine-alternator set (if they are right next to the set).  The start and control batteries shall be marked with the installation date.  Where applicable, the battery stand is to be a heavy earthquake zone installation.  Engine driven alternators/generators shall not be used on a going forward basis for start and control battery charging.

Engines that are rated at 600 kW and larger should have redundant starter motors and batteries.

The engine start batteries shall be floated with a regulated (filtered) charger.  A start battery charger may be mounted either in the control cabinet or mounted on a wall near the start battery stand.  The charger shall have the following:

- output capacity of 2 Amperes minimum

- output Voltage and Ampere meters

- adjustable output Voltage

- internally protected output leads

- high and low Voltage alarms

- charger fail alarm

It is also desirable that the charger have temperature compensation to avoid battery overcharging.

## 7.13	Cold Starting Aids

All water-cooled diesel engine-alternator sets shall be provided with thermostatically-controlled heaters or a heat exchange system, designed to maintain jacket water temperatures not lower than 90 degrees F (per NFPA 110) and not higher than 120 degrees F.  Because traditional electric heating elements wear out, it is desirable to equip the cooling system with manual valves on either side of the heater (as close to the engine block as possible) so that the entire cooling system does not have to be drained to effect an element replacement or heater hose replacement.

For warmer climates, or externally heated engine rooms, it is permissible on dual element heating systems to only connect for half the Wattage output in order to lengthen the life of the block heater system.  For engine-alternator sizes in excess of 750 kW, it is desirable that the heating system have some sort of circulation pump, since natural thermo-siphoning may not provide heat to all areas of the water jacket on these large engines.

Engine rooms (and their ventilation systems for use during engine run) should be designed for a maximum temperature (while the engine is running) approximately 15 degrees F above the ASHRAE maximum summer outside ambient temperature for that location.

For all engine-alternator sets to be installed where outdoor ambient temperatures will fall below 40 degrees F, provisions shall be made to keep the indoor engine room temperature at a minimum of 40 degrees F, or have a battery heater pad that maintains the batteries at that temperature.  It is preferred to have the engine start and/or control batteries at an indoor temperature (when the engine is not running) between 50 degrees and 90 degrees F (see NFPA 110).  The temperature shall be allowed to go up to 120 degrees F if the engine start/control batteries are Ni-Cd.

## 7.14	Acoustic Noise

Sound levels within the building housing the standby plant and outdoor sound levels resulting from operation of this equipment shall meet the requirements specified by OSHA, Telcordia GR-63, and local codes as specified.

Where the engine-alternator set is equipped with a sound attenuating enclosure, the enclosure shall be designed to allow adequate cooling of the engine-alternator set.

Sound-attenuating enclosures, where employed, shall provide hinged doors or latched panels to allow access for normal maintenance and repair operations, including:

- removal and replacement of fuel and lubricating filters

- replacement or cleaning of air filters

- performance of all other normal maintenance operations specified by the manufacturer

Where the engine-alternator set is equipped with a sound- attenuating enclosure; it is desirable that the enclosure cooling requirements be met without booster fans or other accessory devices.

Note:	The supplier must consider widely different climatic zones in Qwest when designing for this requirement.  Some locations will require booster fans or other accessory devices.

Acoustical materials, such as acoustically absorbent liners, shall be non-capillary, non-hygroscopic, free from perceptible odors, and must maintain their acoustic attenuating properties under the conditions of temperature, mechanical vibration, and exposure to petroleum products to which they may be subjected under normal operation.  Elastomeric material used in sealing the acoustic enclosure must remain flexible and resist cracking in the environment they are exposed to in normal use.

## 7.15	Cooling System

The cooling system furnished with the engine-alternator set shall have sufficient cooling capacity to ensure continuous operation at full load at ambient temperatures up to 50 degrees C (122 degrees F) and at the site’s altitude.

Engines may have a switch that shuts down the engine when the radiator fan fails.

Some installations require the radiator and fan mounted separately from the engine-alternator.  This is known as a remote radiator, and the following requirements apply:

- When water flow is produced by the engine driven water pump, total piping pressure drop shall not exceed the engine manufacturer’s recommendation.  If water flow is assisted by an auxiliary pump, piping pressure drop must be matched to pump capacity at desired water flow, per manufacturer specs.

- Remote radiators are designed for installations where no external airflow restrictions occur.  If the remote radiator ventilates a room, has any ducting, or its airflow is opposed by prevailing winds, the cooling capacity is reduced.

- Areas with below freezing temperatures’ will require consideration to protect against ice formation that can block air flow or damage fan blades.

- A remote radiator fan requires an electric motor compatible with the emergency power source.  The Voltage, frequency, and horsepower of the required motor must be specified.  The fan can be direct-drive or belt drive.  If belts are used, multiple belts must be employed to ensure reliability.  An indicator lamp must be on the Engine Control Panel, indicating proper operation of the fan.  The fan motor shall be powered from the engine-alternator it serves.

- Remote radiators shall be grounded to the existing driven ground system if it can be located.  If the existing driven ground system is not available a lead from the remote radiator shall be run outdoors to a point close to the OPGP.  At that point, it may enter the building and tie to the OPGP.  In addition, the external radiator lines will be bonded to the CO’s internal ground system where they enter the building.

- Heat exchangers shall be utilized when the engine manufacturer’s specified maximum head pressures are exceeded.  If a heat exchanger is required, an auxiliary pump shall be used in the system.  The pump shall be powered from the engine-alternator it serves.

- The remote radiator fan shall be rated as "Quiet" with a maximum noise level of 81 dBa measured at twenty-five (25) feet.

When the radiator is mounted on the same sub-base as the engine-alternator, the cooling fan shall be mechanically driven from the engine.  The fan shall be of the pusher type (that is, the cooling air shall be blown through the radiator).  Where the fan is a belt-driven, a redundant belt shall be provided, so that if one belt breaks, the remaining belt(s) shall be capable of driving the fan continuously.

The set-mounted cooling systems as described above shall be capable of operating with total fan head pressure equal to or greater than 0.5 inch of water.

If air intake is provide with ductwork, a flexible radiator section, (rubber or flame retardant canvas type is preferred), shall be utilized to connect the radiator with the ductwork.

Longer-lasting silicone type radiator hoses are required for use in all 3D-condo  buildings.  In other buildings silicone, or teflon, or high-pressure thick rubber hose is most desirable on the hoses that connect to the block heater, but is recommended elsewhere in the cooling system too.

Outdoor enclosures shall provide for access to service the coolant level, a sight glass and low coolant level alarm shall be provided.  Sight glasses shall also be provided for the radiators of indoor engines where the engine is larger than 800 kW.

Louvers on the combustion / radiator cooling / exhaust air openings to engine rooms or enclosures are not absolutely required, nor are filters on the air inlets (filters are a site-by-site decision based on the amount of dust, dirt, and other pollutants that might be drawn in).  However, when louvers are used, they must be powered closed so that they spring open (using a mechanical spring) upon loss of power to the louver motors.  Louver motors should be powered off the engine start-control batteries or off an Essential AC bus.

## 7.16	Safety

The engine-alternator set shall be designed and constructed so that personnel hazards are minimized.  Component parts shall be suitably arranged and/or guards shall be employed to minimize the possibility of accidental contact with hazardous Voltages, rotating parts, excessively sharp edges, and/or high temperature surfaces.

Materials and components employed in the standby AC system shall meet the requirements for fire resistance as stated in Telcordia GR-63.

Exposed equipment surfaces below the 7 foot level where temperatures will rise to greater than 46 degrees C (115 degrees F) shall be marked with warning labels (the warning label does not have to attach to the surface, but can be nearby in a highly visible location – for engine rooms, a warning on the door may be sufficient).  Insulation and/or ventilated guards shall be provided to protect the operator from coming into accidental contact with the high-temperature external surfaces of diesel engine exhaust system parts and piping; plus any other components with surface temperatures higher than 54 degrees C (130 degrees F) when the engine is not running (a general high temperature warning label on an engine room door is sufficient warning for when the engine is running).  Temperature guarding requirements do not apply to outdoor engine enclosures that are not walk-in type (the enclosure provides the personnel protection); nor do they apply more than 7 feet above the ground.

Suitable guards shall be provided for all rotating parts to which the operator might be exposed to, including all fans, blowers, and any other rotating parts of alternators.

- Guards shall be of substantial construction; removable but securely fastened in place and of such design and arrangement that any part of the operators' body cannot project through, over, around or underneath the guard.

- All set screws, projecting bolts, keys, or keyways shall either be suitably guarded or of a safety type without hazardous projections or sharp edges.

- All running gears and sprockets exposed to personnel contact shall be enclosed or be provided with band guards around the face of the gear or sprocket.  Side flanges on the band guard shall extend inward beyond the root of gear teeth.

## 7.17	Hazardous Voltages

Voltages at or above 150 Volts DC or 50 Volts AC rms shall be enclosed or guarded to prevent accidental personnel contact.  Warning labels shall also be provided and conspicuously displayed so that they are visible with guards in place or removed.

## 7.18	Portable Engines and Trailers

The portable engine-alternator (the AC engine-alternator is sometimes incorrectly referred to as a portable generator or genset, since a generator has a DC output) shall meet all requirements of the previous sub-sections of this Chapter, except that grounding conductors need only be sized to meet the NEC requirements)

Although the ratio of portable engines to sites is a local decision, new ones must be equipped as described in this document.  Examples of items to be considered when determining the ratio of generator sets to sites are:

- Area covered

- Number of high priority sites

- Typical weather conditions

- Power company restoration history

- Tolerable down time duration

For engines that are not air-cooled, an engine coolant heater shall be provided that can be plugged into a typical 120 VAC outlet.  The start battery charger will also be connectable to a 120 VAC outlet.

Portables larger than 15 kW shall be mounted on a multiple axle-type trailer that meets all Department of Transportation and local requirements.

- The trailer shall have a locking tool box.  Among the items in this toolbox, there will be four rubber wheel chocks.

- The trailer will be equipped with surge brakes, towing lights (lights, wiring harness, and connector), and an adjustable towing hitch.

- The trailer and portable will have a minimum 100 gallon fuel tank and gauge (or equivalent for LPG tanks).

- Permanently mounted generators or alternators must be grounded to the vehicle chassis they are mounted on.  However, the neutral and ground should not be bonded together at the engine since that connection already exists at the AC meter, and we do not switch the neutral at the transfer system.

All convenience outlets on the vehicle/trailers must be equipped with Ground Fault Circuit Interrupter (GFCI) type protection and must be installed in accordance with current requirements for industrial and/or commercial mobile AC power.  These outlets are intended to provide power for test equipment, power tools, or other similar electrical devices; not power the telecommunications equipment.

## 7.19	Portable Engine Connections

Standardization of portable engine connection hardware is needed to meet the variety of power requirements and the need for a quick positive response during extended power failures.  This section will present the standards for new equipment and enable the retrofitting of existing equipment to company standards.

Portable engine sets shall be grounded according to Qwest Technical Publication 77355 and the NEC.

Sites equipped with a permanent stationary engine-alternator are generally not equipped with portable engine-alternator plugs.  However, for large and important locations, it may be wise to invest in a tap box to allow faster connection of a large rented portable if a serious engine failure occurs.

There are many variations of portable engine-alternators in use by Qwest.  Only units capable of producing single-phase 120/240 Volts AC, with a rated power output from 5 to 40 kilowatts (kW) will be addressed in this section.

Although almost all Outside Plant powering is 120/240 Volt single-phase, some of these sites may be served by engines capable of single or three-phase operation.  These engines are sometimes used with three-phase COs (typically 120/208 Volt three-phase).  For conformity, the 100 and 200 Ampere cords and connectors have been designed to accommodate these types of engines.  The 100 and 200 Ampere inlets have 4 pins, but only 3 of the pins are used on single-phase sites, as shown in the drawings.  The "green-wire ground" is connected to the metallic case of the inlet.

The cable sets illustrated in Figures 7-1 through 7-10 have been standardized for use in Qwest.  The local Power Maintenance Engineer or Inductive Coordination & Electrical Protection (ICEP) engineer should be consulted before length or gauge changes are made to the power cables specified in this document.  Although emergency power cables may be fabricated locally by a licensed contractor, the desired procurement method is through the organizational supply network.  Construction Engineering Memorandum (CEM) 8404 describes and defines the requirements for electrical protection of Outside Plant Electronic Equipment Enclosures.

The purchase of new 10-40 kW 120/240 Volt single-phase engine-alternators may be delayed in locations where existing portable engine-alternators are available.  No Remote Terminals (RTs) have higher power requirements, (RT is a generic name for an Outside Plant electronics equipment enclosure, be it a CEV, CEC, hut, cabinet, etc.).  This initial first cost delay could be cost effective.  It is a local decision to delay the expenditure and should be based on the following:

- The number of Electronic Equipment Enclosure (EEE) huts, CEVs, CECs, UE™s, and CdOs in use

- The number of custom buildings requiring one hundred Ampere emergency service

- The number of engine-alternators and their output rating presently available

- The age of the existing engines, their operational status, and whether or not repair parts can be obtained

- Budget restraints

- Forecasted equipment for each location where a 10-40 kW engine-alternator will ultimately be required

The Ampere rating of the plug chosen (see the Figures) will depend on the ultimate load expected at a given site (this load is to be computed by the Design Engineer, who should then specify the Ampere rating of the AC service).

When calculating the power requirements for RT locations the requirements of the convenience outlet must be included in the total power requirements (convenience outlets on the enclosure must be equipped with Ground Fault Circuit Interrupter [GFCI] type protection).

All hardware, including power panels, cabling, and devices shall be Listed by a Nationally-Recognized Testing Laboratory (NRTL).  Installations shall conform to the NEC and local electrical codes.

Van or truck mounted engine-alternators presently in service capable of producing 120/240 Volt single-phase AC are generally 3.5-13 kW in rating.  They shall be equipped with at least a two pole 30-Ampere breaker.  (The 30-Ampere plug is only actually rated to carry 6.1 kW of 240 V power.  The breaker will protect the cabling, engine, and plugs from having their ratings exceeded.)  As an option, the 30 foot cable may either be permanently attached to the engine-alternator terminal block as in Figure 7-1, or the alternator terminal block may be wired to a Hubbell # HBL-2710-SW twist-lock receptacle.  In which case the alternator end of the cable shall be terminated with Hubbell # HBL-2711 twist-lock plug, (see Figure 7-2).  In both cases the load end of the cable shall be terminated with a 30 Ampere Hubbell # HBL-2713 twist-lock connector.

The DLC housing or power pedestal shall be equipped with a Hubbell # HBL-2715-SW twist-lock inlet.  The 30 foot, 30 Ampere cable in Figure 7-2 is made up of four # 8 AWG conductors in a Type W cable.  (An exception to the use of Hubbell 30 Ampere plugs and receptacles are allowed for existing NEMA L14-30P/R equivalent plugs and receptacles.)

Van, truck, or trailer mounted engine-alternators presently in service capable of producing 100 Amperes of 120/240 Volts single-phase AC shall be equipped with at least a two pole 100 Ampere breaker for single-phase sets, or a three-phase 100 Ampere breaker for three-phase/single-phase sets.  (The 100 Ampere plugs are actually rated to carry only 20.4 kW of 240 V power.  The breaker will protect the cabling, engine, and plugs from having their ratings exceeded.)  As an option the 30 foot cable may either be permanently attached to the engine-alternator terminal block as in Figures 7-3 and 7-5, or the alternator terminal block may be wired to an Appleton # ADR1044CD receptacle.  In which case the alternator end of the cable shall be terminated with an Appleton # ACP1044CD plug, (see Figures 7-4 and 7-6).  In both cases the load end of the cable shall be terminated with a 100 Ampere Appleton # ACP1044CD-RS connector.  The site housing or power pedestal shall be equipped with an Appleton # ADJA1044-200-RS inlet and back box, with pin 3 pulled, and the "green-wire ground" connected to the case.  The 30-foot cable is made up of four (4), number 2 gauge conductors in a Type W, UL sheath.  Engines that are capable of either single-phase or three-phase operation will have five (5) conductor cables.

An exception to the use of 100 and 200-Ampere Appleton plugs and receptacles is allowed where a NEMA equivalent Crouse-Hinds or metallic Hubbell plug or receptacle has the exact same specs as the Appleton part numbers shown in the Figures is already in place.  All new 100 and 200 Ampere plugs and receptacles; however, shall be of the Appleton type.

The existing 50 and 60 Ampere (and other sizes besides 30, 100 and 200 Amp) engine-alternator outputs, power cable sets, and locations equipped with older connection devices should be retrofitted to conform to this document as money is available.  The areas using these devices should migrate their equipment as required by attrition to conform to these specifications stated in this section.  Until "migration" to the new standard is complete, it may be necessary to make adapter cords to match up old engines with new receptacles, and vice-versa.

In some cases, the power requirements of a site served by a portable engine will exceed 100 Amperes.  Van, truck, or trailer mounted engine-alternators presently in service capable of producing 200 Amperes of 120/240 Volt single-phase AC shall be equipped with a two pole 200 Ampere breaker for single-phase sets, or a three-phase 200 Ampere breaker for three-phase/single-phase sets.  (The 200 Ampere plugs are actually rated to carry only 40.8 kW of 240 V power.  The breaker will protect the cabling, engine, and plugs from having their ratings exceeded.)

As an option the 30 foot cable may either be permanently attached to the engine-alternator terminal block as in Figures 7-7 and 7-9, or the alternator terminal block may be wired to an Appleton # ADR20044 receptacle.  In such cases the alternator end of the cable shall be terminated with an Appleton # AP20044E plug, (see Figures 7-8 and 7-10).  In both cases the load end of the cable shall be terminated with a 200 Ampere Appleton # AP20044E-RS connector.  The site housing or power pedestal shall be equipped with an Appleton # ADJA20044-250-RS inlet and back box, with pin 3 pulled, and the "green-wire ground" connected to the case.  The 30-foot cable is made up of four 3/0 AWG conductors in a Type W, UL sheath.  (Engines that are capable of either single-phase or three-phase operation will have 5-conductor cable.)

An exception to the use of 100 and 200-Ampere Appleton plugs and receptacles is allowed where an equivalent Crouse-Hinds plug or receptacle is already in place.  All new 100 and 200 Ampere plugs and receptacles; however, shall be of the Appleton type.

Custom buildings should be provided with a commercial power cabinet or panel, a transfer system, and a distribution panel that receives its power from the transfer system.  This arrangement allows nonessential loads to be eliminated from the emergency power load.

Variations in sites require power load calculations based on each individual installation.  Portable engine power inlets at custom buildings should be sized for the ultimate power requirement of that installation.  The -48 Volt bulk power plant load should be calculated based on all rectifiers being in operation at full rated output (a recharge condition).  During a power failure, the engine-alternator will have to provide power for the equipment and the recharging of the batteries.

In some cases, due to the local power companies, the AC service size they sell is much larger than what we need for the generator, plug, and cord size.  For example, we may only need a 30 Ampere plugs on an 80 cabinet, but the Power Company gives us a 100 Ampere service.  This is generally not a problem because the power pedestal can be equipped with separate breakers for the incoming AC service and the portable engine plug.  However, some local regulators insist that the portable engine plug be the same size as the service.  These cases should be handled individually.  Size the plugs, cords, and engines for a site.  It will not necessarily be the same size as the incoming commercial AC service from the Power Company.

Portable engine receptacles and tap boxes on buildings shall be marked for Voltage, phases, phase rotation (for 3-phase sites), and Ampere rating.

Sequenced instructions for implementing standby power operation should be duplicated and posted in all sites.

Most 3-phase sites will have forward phase-rotation (A-B-C rotation).  However, there are some sites where the commercial feed and all motors in the building will be wired with reverse rotation (C-B-A).  As a general standard, all three-phase alternators, cords, and plugs shall be wired for forward rotation.  Sites with reverse rotation shall have the wiring between the portable engine plug and the transfer system configured so that the forward rotation from the generator becomes reverse rotation at the transfer system.

Figure 7-1: 30-Ampere Cable Hardwired to Single-Phase Engine-Alternator

Figure 7-2:  30-Ampere Cable to Single-Phase Engine-Alternator Receptacle

Figure 7-3: 100-Ampere Cable Hardwired to Single-Phase Engine-Alternator

Figure 7-4: 100-Ampere Cable to Single-Phase Engine-Alternator Receptacle

Figure 7-5: 100-Ampere Cable Hardwired to Three-Phase or Single/Three-Phase Engine-Alternator

Figure 7-6: 100-Ampere Cable to Three-Phase or Single/Three Phase Engine-Alternator Receptacle

Figure 7-7: 200-Ampere Cable Hardwired to Single-Phase Engine-Alternator

Figure 7-8: 200-Ampere Cable to Single-Phase Engine-Alternator Receptacle

Figure 7-9: 200-Ampere Cable Hardwired to Three-Phase or Single/Three-Phase Engine-Alternator

Figure 7-10: 200-Ampere Cable to Three-Phase or Single/Three-Phase Engine-Alternator Receptacle

CONTENTS

Chapter and Section 	Page

8.	Power System Monitor/Controller (PSMC)	8-1

8.1 	General	8-1

8.2 	Standard Monitor and Control Points	8-2

8.2.1	Primary Power Plant	 8-2

8.2.2	Rectifiers	 8-3

8.2.3	Batteries	 8-3

8.2.4	Converter Plants	 8-4

8.2.5	Inverters	 8-4

8.2.6	Residual Ringing Plants 	 8-5

8.2.7	Uninterruptible Power Supplies (UPS)	 8-5

8.2.8	Standby Engines and Transfer Systems	 8-5

8.2.9	AC Power	 8-7

8.3 	Alarms	8-7

8.4 	Statistical Channels	8-7

8.5 	Energy Management and Sequencing	8-8

8.6 	Requirements of a PSMC for Confined Locations	8-8

8.6.1	Primary Power Plant	 8-9

8.6.2	Rectifiers	 8-9

8.6.3	Batteries	 8-9

8.7 	Power Alarms in Sites Without a PSMC	8-10

# 8.	Power System Monitor/Controller (PSMC)

## 8.1	General

The Power System Monitor/Controller (PSMC) provides front-end status for power plants in Qwest.  Control functions (of the DC plant rectifiers) must be provided only when the power monitor is designed as an integral part of the DC power plant controller.  It is recommended that each battery plant have its' own PSMC; however every office should have at least one PSMC for power alarming and monitoring.

The PSMC shall be equipped for remote access dial up capabilities.  Although there may be a proprietary interface, there must also be a dumb-terminal, menu-driven VT-100 interface.

The monitor should have an RS-232 or IP interface such that it can be accessed locally by connection of a cable to a laptop.

All modems/DSUs and PADs shall be DC only.  AC modems/DSUs and PADs are not to be ordered, installed or accepted for use within Qwest.

The PSMC shall be NMA-compatible and support the Qwest TL1 recommended Power message set (see Chapter 13) via X.25 protocol standards (TL1 over IP is optional) for monitors installed in LNS (it is also desirable for NNS-installed power monitors).  The PSMC must be able to simultaneously support dial up capability.  Control functions must not be accessible via dial-up access without a special password.  The installation provider is responsible for verifying that all the alarms are reporting to the proper alarm and NMA center, and note the center responses on the proper form from Chapter 15.

When a larger distribution fuse or breaker does not have a shunt, and monitoring is required, the use of a split core transducer is desirable.  If the BDFB has a shunt then as an option it may be desirable to monitor the BDFB load from the BDFB.  If the Qwest Engineer makes a decision that, a transducer cannot be used or the distance to the BDFB is too great then that Qwest Engineer can waive the requirement for monitoring the BDFB load current, and should note this in the job package.

Alarm and monitoring leads do not require fiber tags, but it is desirable to mark them on both near and far end for source/termination.

Where plant low Voltage disconnects exists, the PSMC shall be connected on the hot side of the low Voltage disconnect circuit of the plant feeding power to the PSMC.

## 8.2	Standard Monitor and Control Points

The following sequence details the desired order of points for equipment to be monitored by the PSMC when a new monitor is placed:

- -48 Volt battery plants

- 24 Volt battery plants

- 130 Volt battery plants

- 24 Volt converter plants

- 48 Volt converter plants

- 130 Volt converter plants

- Ringing plants

- Inverter plants

- Uninterruptible Power Supply (UPS) systems

- Standby engines

- Commercial AC

Many of the monitoring points for standby engines and commercial AC may be furnished as part of the transfer system.  The requisition should list the exact equipment to be monitored and what is to be monitored on each unit of equipment.

The following subsections list the required points to be monitored (if possible).  Optional points should be monitored when the PSMC has the capacity, or when directed by the Qwest Engineer.

### 8.2.1.	 Primary Power Plant

- Analog Points

  - Plant Voltage

  - Plant current

  - Collocation circuits greater than or equal to 60 Amperes requested (basically 75 A and larger fuses or breakers)

  - BDFB feeder current

  - Current of PDF feeders greater than 100 Amperes (optional)

- Binary Points

- Distribution fuse/breaker alarm

- Plant major alarm (this is generally only an output from the PSMC to an alternate alarm system, and not an input into the PSMC)

- Plant minor alarm (this is generally only an output from the PSMC to an alternate alarm system, and not an input into the PSMC)

NOTE:  The power plant major and minor alarms from the conventional controller may be run to a power monitor, but it is better to parallel them to the PSMC major and minor on the e-telemetry device or switch in case the PSMC fails.

### 8.2.2	Rectifiers

- Analog Points

  - Rectifier current, when spare monitor points are available

- Binary Points

- Rectifier Fail (RFA) – Individual RFAs are required unless the controller or monitor has the ability to escalate from minor (single rectifier) to major (multiple rectifiers)

- Low Voltage Disconnect (LVD), if installed

### 8.2.3	Batteries

- Analog Points

- String current – A shunt (minimally sized per Section 3.10, as if it were a disconnect breaker) will be placed in each new flooded battery string to monitor charge and discharge current (this may be pulled off the shunt on a battery disconnect breaker if it exists).  String current is optional for VRLA and Lithium-based battery strings.

- Room temperature – One temperature sensor will be placed to monitor room temperature, approximately five feet above the floor in the area of the batteries.  It must be placed away from heating and cooling sources, such as rectifiers, and HVAC vents.

- Single cell Voltage – The Voltage of at least one flooded cell will be monitored per plant.

- Cell Temperature – Flooded and Lithium-based batteries require one temperature sensor to be placed, to monitor the temperature of one cell per plant.  VRLA batteries require one temperature sensor to be placed in each string, to monitor the temperature of one cell in each string.

- Mid-point Voltage – Measure the Voltage at the midpoint of each battery string (optional).

- Binary Points

- Battery String Disconnect breaker tripped or turned off (if installed).

### 8.2.4	Converter Plants

- Analog Points

- Voltage

- Current (if shunts are already installed)

- Binary Points

- Distribution Fuse fail (possibly both major and minor alarms)

- Converter Plant Major (if available)

- Converter Plant Minor (if available)

- Individual Converter Fail Alarms (CFA) — only required if Plant Major/Minor are not available

### 8.2.5	Inverters

- Analog Points (Optional)

- AC Voltage (per phase, line to neutral)

- Current (per phase)

- Binary Points

- Major alarm

- Minor alarm

- Inverter off normal (indicates when a DC-preferred inverter is in AC-preferred mode or bypass, or when an AC-preferred inverter is in maintenance bypass)

### 8.2.6	Residual Ringing Plants

- Binary Points

- Minor

- Major

- Distribution Fuse Alarm (if available – if not, it must be part of the major or minor alarm)

### 8.2.7	Uninterruptible Power Supplies (UPS)

- Analog Points (Optional)

- AC Voltage (per phase, line to neutral)

- Current (per phase)

- Binary Points

  - Major alarm

  - Minor alarm

  - UPS Fail (if available)

  - Mode indicator (indicates when UPS an on-line UPS is in line-interactive mode or bypass, or when a line-interactive UPS is in maintenance bypass)

### 8.2.8	Standby Engines and Transfer Systems

These points should be installed on a going forward basis.  Older engines and control equipment may not be capable of all of these points.

- Analog Points

- Start Battery Voltage (optional if Start Battery Charger Fail alarm installed)

- Engine Temperature (if available it is optional)

- Engine Oil Pressure (if available it is optional)

- Engine Room Temperature (measured inside the room, not on the outside wall – optional)

- Binary Points

- Engine Run

- Engine Switch Off Normal

- Engine Breaker Open (optional)

- Engine Emergency Stop

- Fuel Heater Fail (when a fuel heater exists)

- Engine Supplying Load or Transfer Switch Proper Operation (optional)

- Engine Fail/Major (generic – use if there are not individual alarms as described below – Engine Fail may be broken out separately)

- Low Oil Pressure (Optional)

- Overcrank (Optional)

- Overspeed (Optional)

- High Coolant Temperature (Optional)

- Engine Minor (generic – use if there are not individual alarms as described above and below)

- Load Transfers (Optional)

- Transfer System Off Normal

- Start Battery Charger Fail (Optional if Start Battery Voltage installed)

- Block Heater Alarm or Low Coolant Temperature

- Fuel System Trouble (or individual alarms below)

- Low Fuel (this may be combined into the Fuel System Trouble)

- Tank Rupture (this may be combined into the Fuel System Trouble) or Tank Leak (including the interstitial space for all direct-buried tanks and any aboveground or underground vaulted tank where the total site fuel storage capacity is 1320 gallons or greater)

- Overfill (can be combined with the Fuel System Trouble Alarm, but in any case, it is required on all direct-buried tanks and aboveground or underground vaulted tanks where total site fuel storage capacity is equal to or larger than 1320 gallons)

### 8.2.9	AC Power

- Analog Points

- AC Voltage per phase/leg – measured phase-neutral, and monitored on the load side of the transfer system

- AC current per phase/leg – monitored on the load side of the transfer system

- Binary Points

- AC fail (although there should be one alarm, individual sensors per phase are desired, if possible).  This should be monitored on the line side of the transfer system (at the main disconnect if possible)

- TVSS alarm (indicates when the TVSS has failed or is degraded – may not be available on older surge suppressors.

For PSMCs that are also the power plant controller, the following control functions will be available:

- Rectifiers

- Re-start (RS)

- Shutdown (TR)

- Sequencing (usually not used)

## 8.3	Alarms

If the PSMC fails, local visual and audible alarms will not be disabled when control is passed to the traditional power plant controller.

The PSMC will analyze incoming alarm information from the power plant components and provide settable downstream alarm levels (thresholds) as required (see Chapter 13).

The PSMC will report at least major, minor, and monitor fail (watchdog) alarms to another alarming system, as a backup to the X.25/IP TL1 communications.

## 8.4	Statistical Channels

The PSMC will be capable of storing statistical data for engineering power plants.  There will be a minimum of ten statistical channels supplied with the PSMC.  Any analog channel can be assigned for statistical data.  Each statistical channel will be capable of storing peak high, hourly average high, daily low and hourly average low for each day while the channel is active.  This data will be retained daily for a minimum of 30 days.

## 8.5	Energy Management and Sequencing

The PSMC will not be wired for power plant or engine control, unless the PSMC is also the power plant controller (then it may control the rectifiers, including energy management and rectifier sequencing).

The power plant controller shall provide energy management as follows:

- The power plant controller will activate sufficient rectifier capacity per controlled plant to support the presented load.

- When energy management is active, the power plant controller will ensure that each rectifier in each controlled plant is active for a minimum of 4 hours during each 30-day period.

- Sequencing priority will be individually selectable by rectifier.

The power plant controller will be capable of providing rectifier restart sequencing to upon restoral of AC power.  The sequencing should be separately controllable for transitions to commercial AC versus the standby engine.  If the transition scheme will not allow two configurations, then the transition scheme must be based on the capability of the standby engine.  Sequencing is not normally employed except in cases of overloaded engines or closed transition transfer switches.

## 8.6	Requirements of a PSMC for Confined Locations

A PSMC for Confined Locations (PSMC-CL) may exist to perform monitoring for locations in Qwest smaller than COs.  A PSMC-CL is optional.  A PSMC-CL may be the same unit as that used for a PSMC in COs, but equipped with fewer points.

A PSMC-CL shall be equipped for remote access dial up capabilities.  Although it may have a proprietary interface on dialup and local RS-232 access, it must also present a dumb-terminal VT-100 menu-driven interface.  The PSMC-CL's modem shall automatically adjust baud rate to match the baud rate of the originating modem with no parity, 8 bits, and 1 stop bit (N81).  The PSMC-CL may be capable of TL1 over X.25 or IP, but it is not required.

The PSMC-CL shall be password protected.  Multiple access levels with “super user” capabilities must be provided in order to make database changes.

The PSMC-CL shall report Power Major, Minor, and watchdog alarms, via dry form C contacts, to the alarm telemetry of the site.

If a PSMC-CL is installed, it should be able to monitor up to 6 battery strings, including the required monitor points specified in the sub-sections below (assume the point is required unless otherwise specified):

### 8.6.1	Primary Power Plant

- Analog Points

  - Plant Voltage

  - Plant Current

- Binary Points

  - Low Voltage (also known as “battery on discharge)

  - High Voltage

  - Power Distribution Fuse/Breaker Fail

### 8.6.2	Rectifiers

- Binary Points

- Rectifier Fail (may be both minor for single rectifier fails, and major for multiple rectifier failures)

### 8.6.3	Batteries

- Analog Points

  - Voltage – Voltage monitoring can be placed on pilot cells/monoblocks (optional)

  - Cell Temperature – One temperature sensor will be placed to monitor the temperature of a "reference" battery in each battery string; preferably the most negative cell on the highest row of the string.

  - Room Temperature – Only one temperature sensor will be placed to monitor room (or cabinet) temperature.  The sensor should not be placed next to a heating or cooling source.

  - String bulk charge/discharge current – A shunt (which may be a part of a disconnect breaker) may be placed in each battery string to monitor charge and discharge current (optional).

  - String float current – A Hall effect sensor (shunts are not sensitive enough) may be placed to monitor string float current (optional).

- Binary Points

- Temperature differential / thermal runaway – the difference between ambient and cell temperature, set to alarm at a certain threshold (per Chapter 13).  This may be a function channel programmed in the monitor.

# 8.7	Power Alarms in Sites without a PSMC

When there is no PSMC for the site the following binary alarms should be connected to the alarm device on site as a minimum (some older power systems may not have all of these alarms available).  When there are older overhead bitstream housekeeping/miscellaneous/environmental alarm systems that do not have enough points, alarms should be combined (minimum of two – major and minor) onto the available points.

- Power alarms

  - Major

  - Minor

  - Low Voltage (also known as “battery on discharge”)

- AC system alarms

  - Commercial Power Fail (at main disconnect if possible)

  - ATS System Off Normal (when there’s a permanent engine on site)

- Engine alarms (when there’s a permanent engine on site)

  - Engine Run

  - Engine Fail

  - Engine Emergency Stop

  - Low Fuel (can be part of Fuel System Trouble)

  - Fuel Leak / Fuel System Trouble – from fuel monitor if available

  - Fuel Heater Fail (when there is a fuel heater)

  - Engine Low Start Battery (when available from the charger)

  - Engine Start Battery Charger Fail

CONTENTS

Chapter and Section 	Page

9.	DC Power Distribution	9-1

9.1	General	9-1

9.2	Telecommunications Equipment Loads	9-1

9.3	Power Plant Distribution Characteristics	9-6

9.4	Cabling and Bus Bar	9-7

9.5	Protectors and Cable Sizing	9-11

9.6	Fuse Sources	9-13

9.7	Bus Bar Labeling and Layouts	9-23

Figures

9-1	Switch Distribution Voltage Drops Loop	9-4

9-2	Equipment Distribution Voltage Drops Loop	9-5

9-3	Voltage Drops from Battery Strings to PBDs	9-5

9-4	Typical Mounting of a Bus Bar above PDFs and Battery Stands	9-11

9-5	BDFB Fuse Assignment Label	9-16

9-6	Typical Layout of BDFB Fuse Panels	9-17

9-7	Typical Layout of 2 Load 600 Ampere BDFB	9-18

9-8	Typical Layout of 4 Load 400 Ampere BDFB	9-19

9-9	Typical Return Bus Bar Mounting for a 7’ BDFB (View A-A)	9-20

9-10	Typical Return Bus Bars Mounting for a 7’ BDFB (View B-B)	9-21

9-11	Load and Embargo Labels for BDFBs	9-22

9-12	Example of Bus Bars (Term Bars) above a Battery Stand	9-23

9-13	Example of a Battery Return Bus Bar above a BDFB	9-24

9-14	Chandelier Hot Side Main Terminal (Term) Bar	9-24

9-15	Chandelier Return Side Bar	9-24

9-16	Example of a Remote Ground Window	9-25

9-17	Example of a Main Return / Ground Window MGB Bar	9-25

9-18	Example of Sandwiched Terminations	9-26

# 9.	DC Power Distribution

## 9.1	General

This unit describes the engineering requirements for DC distribution.  Qwest is responsible for the floor plan(s) layout of a site.  Layouts of equipment shall be per Qwest Technical Publication 77351, Qwest Standard Configuration Documents, and Telcordia GR-63, as required.

### 9.2	Telecommunications Equipment Loads

The power load that the DC distribution system feeds is determined by the type, quantity, and mix of telecommunications equipment in an office.  Once the load has been determined, it must be matched to a distribution system and to a power source with adequate capacity to power the loads after overcoming distribution losses.  The power cable shall be sized according to the Voltage drop guidelines of this section.  Ampacity of the cable shall be equal to or exceed the protector (fuse or breaker) size.

The nominal Voltage levels for standard telecommunications equipment are 24, 48, and 130 VDC.  Although nominal Voltages are standardized, the operating Voltage limits permitted on individual equipment assemblies are more variable.  For example, NEBS specifies that nominal -48 VDC equipment must work from -42.75 to -56 V.  However, some older equipment won’t work up to the -56 V (some might only work to -54, for example), while other more modern equipment might work above it (60 V, for example).  Most equipment will work down to at least -42.75 V, and some will work to an even lower level (-39.5 V, for example).

The formula for calculating Voltage drop is:

- CM = Circular Mils (available for cable from NEC Chapter 9 Table 8, or from Section 9.11 of Tech Pub 77350; and calculable for bus bar cross-sections based on a circular mil being equal to the area of a circle 1/1000 of an inch in diameter)

- I = Amperes (List 2 drain, half the protector size, battery discharge rate, etc.)

- K= 11.1 for copper and 17.7 for aluminum

- d = distance (for distribution, this is top-to-top distance and does not include the drop cabling into or out of equipment or distribution bays)

- VD = Voltage drop as described in the rest of this section

This formula can be used for one-way (feed or return) calculations, or loop distances (feed and return distance and Voltage drops combined).

The requirements for distribution Voltage drop, and which drains to use for sizing are specified in the following paragraphs, and illustrated in Figures 9-1, through 9-3.  These Figures and the following bullets are designed around nominal -48 V battery/rectifier and converter plants.  For nominal 24 V output, cut the Voltage drops in half.  For nominal 130 V output, double the allowable Voltage drops.  For converter plants, convert the rectifiers of the figures to represent converters (obviously converter plants won’t have batteries either).

- The 0.10 (or 0.05 for NNS) one-way Voltage drop from the "chandelier" negative bus to the primary power distribution boards/bays/panels, shall be calculated to the bus bar Ampacity of the distribution bay/panel (unless the shunt capacity of the plant is less, in which case it may be calculated at the plant’s main shunt capacity).  The 0.10 (or 0.05 for NNS) one-way Voltage drop from the chandelier positive bus to the plant return bar(s) is calculated at the Ampacity rating of the shunt.  The shunt(s) in the chandelier or PBDs also have a maximum Voltage drop (typically 0.05 V — 50 mV).

- Battery cable, from the overhead bus bar above the battery strings to the main bus bar chandelier shall be sized to either the 4 or the 8 hour discharge rate (see Chapter 2 for rules on whether the 4 or 8 hour rate is to be used).  This is depending on the site’s reserve time of the batteries at 1.86 Volts per cell (or 1.88 V/cell for NNS), using a 0.20 loop Voltage drop (or 0.1 V loop for NNS).  Where 2 strings exist on a stand (or the potential for two strings exists on a stand) that use common termination (term) bars for both strings, the 4 or 8 hour rate of the batteries is doubled for the Voltage drop sizing.

- For new bus bar plants that do not have a "chandelier" (all battery strings are cabled directly to the main busses above the PBDs), their cables are also sized at the 4, or 8 hour rates using a 0.4 V loop drop (0.25 V loop for NNS).

- The switch manufacturer's recommended total List 2 drain for the PDF, and the 1.0 V loop Voltage drop shown in Figure 9-1 shall determine the cable size from the power board to the PDF.  The manufacturers' recommended drain shall also determine the fuse or circuit breaker size for the power board.  It is switch Engineering/installation’s responsibility to run and size the battery feed and return cables from the main power board.

- The Voltage drop, cable sizing, and drain from the switch secondary distribution (PDF) to the switch bay shall be determined by the switch manufacturer (see Figure 9-1).

- Any feeder from a power board to a BDFB/BDCBB should generally be protected based on a load of 225-400 Amperes for quadruple (4) loads, or 400-600 Amperes for dual (2) loads.  Exceptions can be made based on the size of the panels and the loads at the BDFB/BDCBB.  The cable sizing for this loop should be computed based on half the protector size used as the drain.  However, cable Ampacity shall always equal or exceed the protector size.  BDFB/BDCBB loads are limited to one half of the protector size on any one side of the feed (A or B, C or D, etc.) so that one side can carry the whole load if the other side fails and there is true redundancy in the equipment.  For example, if we were feeding A and B panels on a BDFB/BDCBB with a protector size of 500 Amperes, the Voltage drop calculation would be done at 250 Amperes (since any one side should normally not carry more than that).  Cable Ampacity would still need to exceed 500 Amperes in this example.

- Each distribution fuse panel in a BDFB/BDCBB shall be individually fed.  All feeds to a given BDFB/BDCBB shall originate in the same power plant.  The conductor(s) shall be, at a minimum, sized for the protection device and be increased in size as required to allow the total Voltage drop to not exceed 0.5 Volts one way, or 1 Volt loop.

- The maximum allowable loop Voltage drop from the BDFB/BDCBB to any facilities (non-switch) equipment shall be 0.25 Volts (0.75 V for NNS), based on the List 2 drain of the equipment expected in the bay.

- Follow the recommendations of the manufacturers of the equipment expected in a bay for the protector sizing for a bay receiving a miscellaneous fuse or breaker panel.  Lacking that information, add up the expected List 2 drains of the equipment expected to be fed from that panel.  Calculate the Voltage drop cable sizing for the miscellaneous fuse panel based on the given List 2 drain for the bay, or 80% (the inverse of the 125% protector sizing rule) of the feeder fuse or breaker size.

- Note also that most loads fed from a miscellaneous fuse or breaker panels go to equipment that can switch from “A” to “B” supplies if one supply fails.  These will double the load on the remaining fuse panel supply fuse.  Therefore, the feeds to the panel must each be sized (have an Ampacity) to handle both loads.  The Voltage drop calculation need only be sized for one load.

- Feeds to miscellaneous fuse panels feeding only DSX bays are exempt from Voltage drop standards, and can be fed with wire meeting the minimum Ampacity of the feeding fuse.   These fuses feed only LEDs (non-service-affecting) and a single feed miscellaneous fuse panel feeding many bays is the general method of providing power.  Very few LEDs in the lineup will be fed at any one time.  In order to qualify for this exemption, the miscellaneous panel must be marked as “DSX Only”.

- Equipment fed directly from the power distribution board/bay (usually OSP equipment, CdO equipment, cabinetized high drain equipment, or equipment fed from a distributed power plant in a larger CO) should have the cable sized based on the List 2 equipment drain provided by the manufacturer, and with a loop Voltage drop of 1.25 V (1.75 V for NNS).

Every equipment bay and/or shelf which includes any Designed Services Circuits (coin, ISDN, 56kb, FXS, FX0, DX , TO etc.), and/or DS1/T1 (or higher data rate) circuits must be fed independently from both the "A" and "B" power source (primary and/or secondary distribution).  Equipment bays and/or shelves, which include only less than 1400 DS0 and/or POTS circuits are not required to have A and B feeds.

Mounting of more than one wire/cable, terminal end on a single lug (this practice is commonly referred to as “double-lugging”) is prohibited.  A splice or tap should be used instead.

Input power connections to the using equipment should be of a crimped lug type.  If plastic connectors are used they shall not protrude from the front or rear of the equipment where they may be inadvertently knocked off or loosen.

Figure 9-1:  Switch Distribution Voltage Drops Loops

Figure 9-2:  Equipment Distribution Voltage Drops Loop

Figure 9-3:  Voltage Drops from Battery Strings to PBDs

All new battery cables (both feed and return) from the battery bus bar to the main battery bus bar chandelier (where one exists) will be sized per figure 9-3.  If a battery disconnect is required, size the battery cables using Chapter 3.  Unfused battery cables must be sized as follows:

- Batteries less than 840 Amp hours:  Ampacity to exceed disconnect device sizing (even if it does not have a disconnect) as stated in Section 2.5

- Batteries 840 Amp hours to 1700 Amp hours:  four 4/0 AWG

- Batteries over 1701 Amp hours:  four 350 kcmil

## 9.3	Power Plant Distribution Characteristics

Protectors (fuses or circuit breakers) being fed from a converter plant or a ringing plant shall NOT exceed or equal the capacity of the plant.  An example would be that a 2-Ampere ringing generator shall not have a fuse larger than 1.33 Amperes to the using equipment.

Distribution fuses and circuit breakers shall not be multipled (e.g., daisy-chained) between loads or equipment bays.  This means that a single fuse or breaker can’t feed two or more separate busses (unless the busses are bonded together by bus work and labeled as a single bus).  Ringing distributing is exempted, as defined in Chapter 10.

Circuit breakers may be capable of being alarmed either in the tripped (known as mid-trip or electrical trip alarm), or both the tripped and off positions (the off position is referred to as alarm on mechanical trip, so a breaker capable of alarming in both conditions is sometimes referred to as mechanical and electrical trip, while a breaker that alarms only in the tripped position is sometimes referred to as electrical trip only).  Breakers 100 Amps and larger should generally be both electrical and mechanical trip, while smaller breakers may be mid-trip only.

To design a distribution system, the following characteristics of a power plant must be determined:

- Plant Voltage limits

- Protection requirements

- Capacity and size of charging equipment

- Ultimate current drain required of plant (using a combination of existing peak drain of the plant over the last year, List 1 drains of Qwest equipment to be added, and ordered power from Collocators)

- Physical relationship of the plant components based on floor space configuration

- Grounding requirements

DC/DC converters that are placed for equipment isolation should be physically located in close proximity to the served equipment.

## 9.4	Cabling and Bus Bar

Cables or bus bar carry the current from the rectifiers to the batteries, from the batteries to the discharge panel, from the discharge panel to any converter plant or other distribution, and/or to the loads, and then back to the batteries and rectifiers in the grounded return lead(s).  Whether cables or bus bars are used, each type of conductor must be capable of carrying current to or back from its loads without overheating or exceeding the Voltage drop requirement.

Stranded copper wire used in AC and DC circuits operating at less than 600 Volts rms is primarily insulated with one or more of the following compounds: flame-retardant synthetic or mixed rubber, e.g., styrene butadiene rubber (SBR), ethylene propylene rubber (EPR/EPDM); chlorosulfonated polyethylene (CP); thermoplastic elastomer (TPE); polyvinyl chloride (PVC); non-halogenated materials (e.g., polyethylene-co-vinyl acetate thermosets), or EPDM-CP composite structures.  The chief compositional distinctions between insulation materials that lead to functional consequences for power cable products are whether these insulations contain either lead or sulfur.  Concerns about lead compounds arise from environmental regulations, pollution impacts, and high costs of landfill disposal.  Elimination of lead coatings (such as traditional “tinning”) and lead-based stabilizers could result in copper corrosion, reduced electrical performance in humid and moist environments, and/or thermal degradation of insulation materials (although advances are being made in non-lead materials due to RoHS requirements).  Sulfur compounds are often used to promote or form cross links within rubber thermoset materials.  These cross linked materials are resistant to chemical and mechanical degradation as well as dimensional distortion at high temperatures.  However, the sulfur can react with the copper and accelerate corrosion.  Given these considerations as well as the cold flow properties of the insulation type, two major areas of distinction are made between power cable products:

- Sulfur-containing insulations and all other insulations

- Cables with a braided cotton covering (treated for flame retardancy) and those without this covering.

Depending on the specific application, one wire or several wires in parallel may be used, and for DC application, they will generally be placed on cable rack (some small circuits may be run in conduit, or attached to the outside of cable rack, or run on cable rack hangers).

The power wire types that are approved for use within Qwest are THWN, THW, or THHN for AC: and XHHW, RHW-LS, RHH, and TFFN with cotton braid for DC wiring in the racks.  For 12 AWG and smaller wiring within a bay, although RHW, RHH or XHHW is preferred, THWN, THHN, and TFFN may be used where protected from abrasion and coldflow at impingement points.  TFFN without cotton braid may also be used in conduit or attached to the side of the rack (when attached to the side of the rack, it must be protected from abrasion and coldflow at points of impingement).

Single conductor, whether solid or stranded is usually called wire; whereas cable is generally an assembly of two or more conductors in a common insulating sheath.  The following are the power wire gauges most commonly used within Qwest: 14 AWG, 12 AWG, 10 AWG, 8 AWG, 6 AWG, 4 AWG, 2 AWG, 0 AWG (also known as 1/0), 00 AWG (also known as 2/0), 0000 AWG (also known as 4/0), 350 kcmil (formerly known as 350 MCM), 373 kcmil (flexible wire only), 500 kcmil (formerly known as 500 MCM), 535 kcmil (flexible wire only), 750 kcmil (formerly known as 750 MCM), and 777 kcmil (flexible wire only).

Solid wire is sometimes used, especially in the smallest sizes; however, power cable is generally stranded.  There are two primary types of stranded wire used.  Class B stranding (per ASTM B8) is known as “Standard”.  Typically flexible power wire used in telecommunications applications is finer/smaller Class I stranding (as defined by ASTM B172).  In some cases, even finer stranding is used in flexible wire, such as Class K (per ASTM B174).  Class K is sometimes referred to as diesel locomotive (DLO) cable.  Class K is also sometimes referred to as “super-flex” or welding cable.  Although not an official designation, welding cable is also sometimes referred to as Class W.

For insulations containing halogen (soft-rubber styles of RHH or RHW), with or without the cotton braid, the conductor must be copper and tinned.  All power cables used near flooded lead-acid and Ni-Cd batteries must be tinned to provide extra protection to the strands from the acid (or alkaline) vapors that may be given off by the batteries.

Non halogenated thermo cross linked wire (all XHHW and some types of RHW or RHH) does not require a cotton braid or to be fiber wrapped at lacing points.  Nor does it require tinning outside the power room (there are no halogenic or sulfuric compounds to attack the copper).  The exception is for class I type wire, which must be tinned (since it is likely to be used in the power room, near the batteries).

To distinguish RHW or RHH  without a cotton braid that must have fiber wrapping at tie and impingement points from RHW or RHH that does not need it at the tie points, the non-halogenated thermo cross linked RHW or RHH without a cotton braid shall be marked from the manufacturer.  DC cotton braid or XHHW wire colors shall be gray, green, or black (green is obviously for grounding, and while gray or black can be used on positive or negative leads, if the colors are different for positive and negative, the gray is preferred for the grounded return side [usually positive]).  The DC thermoset cross-linked RHW or RHH wire without a cotton braid shall be gray marked with a blue or black tracer, black marked with a red or white tracer, and the green wire shall be marked with a yellow tracer.  Red DC wire color is only allowed in in-bay wiring, and on wiring harnesses, and in circuits where 16 AWG or smaller wiring is used; and even then it is discouraged, and must be labeled at both ends for polarity.

Cables and bus bar must be copper.  Cables must meet the requirements of Telcordia GR-347-CORE, “Generic Requirements for Central Office Power Wire”.  Ampacity for the wire shall be per Qwest Publication 77350 and NEC Table 310.16.  Cable Ampacity shall be at the 75ºC rating for wire sizes of No. 1/0 AWG or larger, and at the 60ºC rating for wire sizes No. 2 AWG and smaller (unless all terminations and wires are Listed and marked for a higher temperature).

The minimum distance between the bus bars and any other object shall be in accordance with Qwest Pub 77350.  This includes hot, return, and grounding bus bars.

Cables from the rectifiers to the batteries, between battery stands, and from the batteries to the discharge panel will be on a separate cable rack from all other cables when they are not protected by a battery disconnect.  These cables are generally referred to as non-fused (or un-fused) cables.

Cable rack "power cable brackets" mounted to the cable rack at eighteen inch intervals may be used in LNS for power cables fused (or breaker protected) at 70 Amps or less, and smaller than 4/0 AWG, only when small quantities of cables are required.  Adhere to the stacking height limitations for brackets listed in Tech Pub 77350.  The use of segregated cable racks for power and switchboard cable is the first choice of installation in central offices.  All power cables larger than 4/0 AWG, regardless of protector size (and all power cables regardless of size in NNS) shall be run on dedicated fused power cable only cable racks (Reference Tech Pub 77350).  The placement of any type of cable used for anything other than power on fused power cable only racks is strictly prohibited.

Dedicated fused power cable only cable racks shall not be equipped with screens, pans, or cable horns.  T-intersections and/or 90 degree turns in the racks require corner brackets in order to maintain the minimum bending radius of larger size cables.  All cabling on these racks shall be secured per Tech Pub 77350.

Power cables (Battery and Battery Return) on unsecured cable racks shall be closely coupled and paired securely together at 24 inch maximum intervals.

Primary DC power distribution is defined as leads from the power plant to the BDFB (feeder conductors) or switch PDF, or directly to equipment bays.  Secondary DC power distribution is defined as power from the BDFB or PDF to the equipment bays (load conductors).

The cable between the Power Distribution Boards/Bays, Batteries, and Rectifiers should generally be of the flexible type.  Drops into equipment bays 4/0 or larger should generally be of the flexible type.  For entry into Power Boards the tap should be within 15 horizontal cable rack feet.

All wire shall be Listed with copper conductors, have an oxygen index (LOI) of 28% minimum, and a UL 94-V0 rating.  (Wire used internal to the Power Plant bays, and the Power Plant manufacturers' recommendation for wires connected to the protection devices shall be exempted from the above rule.)

It is also a requirement in Qwest that all cable rack located in the Power room or area be engineered and installed according to Qwest Technical Publication 77351.

Armored power cable shall be no longer than three feet in length, except for vertical runs in manufacturer's equipment, and shall never be run on a cable rack with switchboard or other power cable.  Insulation coated (liquid tight) armored power cable can be longer than three feet and shall be suspended beneath the power cable rack or run on a separate cable rack for power equipment applications only.  When insulation coated armored power cable is suspended, it must be supported every two feet.  Armored cable outside the power room must be placed in accordance with Qwest Technical Publication 77351.

Cable temperature shall not exceed 115 degrees F in any horizontal cable rack.  In addition, there shall be no instance where an equipment surface temperature exceeds 115 degrees F without a highly visible warning label.  Cable temperature in the vertical riser within the bay to the overhead rack may exceed 115 degrees F.  However, if the cable temperature in any vertical riser within a bay is going to exceed 125 degrees F, there will be a highly visible warning label.

If the battery return bus is used as the MGB in the ground window, the bar(s) and the interconnecting copper bus(s) must be sized to meet the ultimate Ampacity of the Power Plant.  See Qwest Technical Publication 77355 for separation and sequencing of connections.

The battery return bus should be placed above the Power Boards (or internal to them in small toll load only plants) unless it cannot physically go there (or there are cable access issues).  If it can’t go there, an attempt should be made to get it as close as possible, and in no case should the distance exceed 30 feet.

The battery feed and return bus bars (in the cases where they are both above the equipment rather than one or both being internal to the equipment bays) shall not be stacked.  The hot and return bus bars shall be isolated on the cable rack and spaced a minimum of 1'6” from each other, per figures 9-4 and 3-2.  Exceptions are allowed for the battery return bus bar for a BDFB, for the main charge/discharge bus, battery return bus bar, battery stands (see section 3.9.4), and the ground window bars.

Battery and battery return bus bars must be labeled with the power plant potential (-48V, +130V, -130V, +24V, -24V, etc.) for the hot bus, and as battery return.  Labeling shall be per the requirements of Qwest Technical Publication 77350.  The battery return must not be labeled as a grounding bar, except when it is the MGB in the ground window (per Qwest Technical Publication 77355).

Figure 9-4:  Typical Mounting of Bus Bar above PDFs and Battery Stands

## 9.5	Protectors and Cable Sizing

Since smaller capacity protectors will operate more quickly in the case of resistive faults, they should be sized as close to 125% of the peak currents (List 2 drain) as practical (and generally should not be more than 200% of that List 2 drain unless there is no standard fuse size between 125 and 200%).  Protector selection also establishes the minimum allowable cable size.  Cable sizes may be increased above the minimum to meet Voltage drop requirements (and usually are for 24 and 48 VDC systems).

The discharge and distribution protectors must be engineered for each application and must have a current rating that will protect their cables.  For example, a standard 1/0 AWG cable, which can carry 150 Amperes, should always be protected by a fuse or a circuit breaker no larger than 150 Amps.

The protector size should not be subsequently oversized if larger conductors are furnished to meet the Voltage drop requirements.  Protectors should not be so close in size to peak loads that nuisance protector operation or overheating of the protector occurs.

These protector sizing rules do not apply to fuses or breakers which feed BDFBs from the primary PBDs (main Power Board).  For rules on sizing of fuses and breakers that feed BDFBs, see Section 9.2.

Cable sizing for the battery charge cables (from battery bus bars to main chandelier or directly to the plant busses) should be based on the Ampacity of the batteries at the four or eight hour rate to 1.86 Volts per lead-acid cell (unless a higher rate battery is used for DSL backup; in which case that higher rate shall be used) or equivalent for other battery types.  If the battery stand is a two string stand using only one battery string, it is recommended that cabling be sized as if there are two strings on the battery stand.

It is also recommended that the feeder cable(s) from the PBD to the BDFB be sized to the full Ampacity of the largest possible feeder fuse or breaker for that BDFB, (e.g. 600 Amperes) regardless of the present size of the breaker or fuse protecting the circuit.

Cables are sized in the following way.  First, determine the appropriate cable path for power cables through the office following existing or new cable rack routes to determine the cable length.  This length is determined by TOP TO TOP measurement.  Top to Top is from the top of the power bay to the top of the use equipment bay.  Then, cable sizes should be selected to meet the requirements discussed herein.  To do this, size each cable for the ultimate simultaneous average busy season busy hour drains (List 2) it will carry.  If the drains are variable, a peaking factor of 1/3 must be added.  Fuses should be selected for the application used, and not the maximum drains the cable can carry.  Care should be taken with feeds and protection to devices that have A & B inputs and are switching capable, as in the case of certain fuse distribution panels (FDPs).  In these cases, both A & B feeds need to be sized to handle both loads on either feed.

All fuses and circuit breakers must be Listed and rated for the available fault current.

All protection devices (fuses and circuit breakers) must be AC rated for AC circuits and DC rated for DC circuits (some are rated for both, and that is acceptable as long as the Voltage to which they are exposed does not exceed their rating for that particular type of electricity).  The fuses must be color coded to prevent mixing.  AC rated fuses include but are not limited to FRN-R and NON types.  DC rated fuses include but are not limited to TPA, TPN, TPL, TPJ, TPS, GMT, and 70 types.  GMT and 70-Type fuses are not only commonly used in DC circuits, but may also be used for ringing (since they are rated for both the AC and DC Voltages in ringing circuits).  TPN type fuses (or another equivalent DC-rated and Listed fuse from another manufacturers that fits the fuse holder) must be used on a going forward basis (new fuses) in existing DC applications that formerly used the FRN and NON (RK1 & RK5 rated) types (although those types have DC ratings, they were not truly designed for DC).

Renewable link and H type fuses are not acceptable for use on a going forward basis.

When a DC fuse requires an accompanying alarm/indicating/pilot fuse, the pilot fuse used should be of the size and type required by the fuse block manufacturer to avoid nuisance blowing of the fuse on under sizing and overheating of the bypass resistor on over sizing.

Circuit breakers shall be of the thermal-magnetic or magnetic type and shall be Listed.  They shall be trip-free types.  Contacts shall not be able to be held closed during an overcurrent condition, by holding the lever in the closed position.

Circuit breakers must be DC rated for DC circuits and AC rated for AC circuits.  They cannot be intermixed and must be clearly marked as either an AC or DC breaker (they may be marked as both, and that is acceptable as long as the Voltage to which they are exposed does not exceed their rating for that particular type of electricity).

Switches shall meet all the requirements of the applicable UL and ANSI Standards.  Ferrous materials shall not be used for current carrying parts.

## 9.6	Fuse Sources

There are various types of fuse and breaker sources.  From the DC power plant, there may be up to three fuse or breaker panels between the plant and the equipment (see below), or the equipment shelves can be fed directly from a PBD or BDFB/BDCBB:

- Primary Sources located at the power plant (PBDs)

- Secondary Sources:

  - Battery Distribution Circuit Breaker Boards (BDCBB)

  - Battery Distribution Fuse Board (BDFB)

  - Power Distribution Frames (PDF) in switches (they have various names)

  - Coded frame fuse panels associated with specific equipment

  - Older Fuse Bays (FB)

- Secondary/Tertiary Sources:

  - Miscellaneous fuse panels at the top of individual bays

  - Miscellaneous breaker panels at the top of individual bays

Distribution leads leaving the bay almost always leave from the top of the bay.  Incoming power leads to a bay also generally enter from the top of the bay.  The exceptions to this are when the secondary fuse source is mounted on a raised floor, or when Qwest Real Estate approves the drilling of the floor underneath a primary or secondary fuse source bay, in writing.  Qwest Real Estate is solely responsible for core drilling floors in a Central Office environment.  No installation supplier or contractor (unless hired by Qwest Real Estate) is authorized to perform the core drilling function.

Tag both ends of every power, power return, and ground lead as instructed in Qwest Technical Publication 77350, "Central Office Telecommunications Equipment Installation, and Removal Guidelines”.

A separate battery return lead will be paired and sewn together or otherwise closely coupled with each distribution or source lead whenever possible.

- This "pairing" requirement does not apply to cabling between the power plant and batteries and/or primary distribution board, or the cable within a few feet of the return bus of a secondary distribution center — e.g. BDFB.

- It also is not required for Outside Plant applications where the DC plant size does not exceed 100 Amperes.

- In cases of a remote ground window where the served equipment is not on the same floor as the remote ground window, the battery feed leads do not have to be paired with the battery return leads all the way to the ground window.  For the portion of the run where the battery feed and the battery return leads are not paired, the battery return lead shall be paired back on itself, (this includes going though the same cable hole).  The total impedance of the battery feed and the total impedance of the battery return must be equal (i.e., the Voltage drop must be divided equally between the battery feed and the battery return — 0.5 V one-way drop for both the feed and return).  Refer to Qwest Pub 77355 for ground window guidelines as required.

- Between the bays and/or battery stands, internal to the power plant, paired battery and return are preferred.  However, unpaired leads are allowed internal to the power plant.

The battery return lead will be separate and isolated from the building ground.  Specifically, frame ground return for equipment power should not normally be allowed on new equipment.  If a supplier chooses to combine the battery return with the building ground, the equipment must be:

- Electrically isolated from the floor and ceiling.

- A minimum of six feet from any other equipment.

Fuse panel vertical bus bar shall be used to interconnect the individual panels.  All of the fuses connected to one supply lead must be in one group on each bay, but there may be several groups on one bay which are connected to different supply leads (A and/or B supply).  Under no conditions will the "A and B" sources be tied together at a fuse panel.  Interbay bus bars are available if the fuses in one group require more than one bay.

Fuse reducers will not be used in "dead front" DC fuse panels or any AC panel.  A "dead front" panel is defined as a fuse block with a cover on it.  Fuse reducers shall only be used on "open face" fuse panels.  "Open face" is defined as fuse panels in which the fuses are on the front and external to the panel face.  Double fuse reducing (using more than one pair of reducers) is not permitted.

All fuse and circuit breakers for power boards shall be numbered according to the Qwest standard configuration for that power plant (see Chapter 2).

The largest output fuse or breaker to be mounted in a BDFB/BDCBB shall be 150 Amperes.  Some BDFBs do not allow fuses that large, and some require spacing around the fuse for sizes larger than 60 Amps.  Do not exceed the largest fuse size possible for that specific BDFB, and follow manufacturer guidelines for spare positions if necessary (using larger fuse sizes that require surrounding spare positions for heat dissipation should be avoided in fuse panels because its too difficult to ensure that the “spare” spaces will never be used; however, fuse blocks that take two positions can be used).

The largest output distribution cable size to be run within the BDFB/BDCBB shall be a 1/0 AWG (BDFB/BDCBB feeder wires are exempted).

Blank panels on the BDFB/BDCBB shall be used in the following locations:

- Top panel

- Bottom panel

- Between panels, where there is a potential difference of more than 140 V between the panels

- Unequipped positions (a guard may be placed over an unequipped position in a BDCBB, or the entire BDCBB must have a cover or door if there are exposed, unequipped positions)

Fuses shall be assigned starting on the bottom panel of each group and from left to right when facing the front of the assembly.  Fuse panels should be equipped from the bottom up in top fed BDFBs.

A BDFB/BDCBB located on one floor shall not be used to supply equipment located on another floor.  Feeds from BDFBs to Collocators — Virtual or Physical CLECs — can be exempt from this rule.

For all new BDFB additions, configurations of battery return bus bar are to be mounted in the immediate area above the BDFB framework, (see figurers 9-9 and 9-10).  This bus bar will provide termination for calculated battery return feeders from the power plant, and for the returns from the secondary distribution leads leaving the BDFB.

The battery return will be sized with up to 750 kcmil cable using the same engineering criteria as the power feeders for the BDFB.

The maximum continuous drain on each feeder to a BDFB shall not exceed one half of the protector (fuse or breaker) size for that BDFB.  For example, for a BDFB protected at four hundred (400) Amperes (load A or B) the maximum continuous drain for each load (A or B) shall not exceed two hundred Amperes.

Each distribution fuse panel on the BDFB shall be labeled with the Voltage and polarity of that panel.  Each fuse position 01 through XX on each of the panels shall be labeled both front and back to indicate its' location.  Each fuse panel shall be labeled to indicate the panel's position within the BDFB, 1, 2, 3, or A, B, C, etc.  Typical arrangements are shown in figures 9-5, 9-6, 9-7, and 9-8.

All fuse positions should be installed and assigned from the bottom up to avoid cable congestion and for the safety of the installer adding future fuses.

For any additional fuse panels added to the BDFB after the initial order, the panel position, Voltage, and polarity shall be labeled by the installer.

The installer shall stamp the load designations on the fuse labels and the meter load designation label.  Reference loads with alphabetic characters (A, B, C, D, etc.).  Panels linked together with a bus bar will have the have the same load designation.

The battery feed and battery return cables shall be labeled on both ends using a designation tag to indicate the other end of the cable, per Qwest Technical Publication 77350.

The following sign should be placed on the BDFB.  The sign should be visible and clear.  The size of the sign should be 3 inches by 4 inches.

Figure 9-5:  BDFB Fuse Assignment Label

All BDFBs should be installed and labeled as the figures 9-6, 9-7, and 9-8 indicate.

|  | -48 Volts |  | 01 |  | 01 |  | -48 Volts |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 02 |  | 02 |  |  |  |  |  |
|  |  |  |  | 03 |  | 03 |  |  |  |  |  |
|  |  |  |  | 04 |  | 04 |  |  |  |  | Fuse Blocks |
|  |  |  |  | 05 |  | 05 |  |  |  |  |  |
|  | PNL # | LOAD |  |  |  |  |  | PNL # | LOAD |  |  |
|  |  |  |  | 06 |  | 06 |  |  |  |  | Panel number !,2,3,etc |
|  | 01 |  |  |  |  |  |  | 01 |  |  |  |
|  | 02 |  |  | 07 |  | 07 |  | 02 |  |  | BDFB Load (A, B, C. etc. |
|  | 03 |  |  |  |  |  |  | 03 |  |  |  |
|  | 04 |  |  | 08 |  | 08 |  | 04 |  |  |  |
|  | 05 |  |  |  |  |  |  | 05 |  |  |  |
|  | 06 |  |  | 09 |  | 09 |  | 06 |  |  |  |
|  | 07 |  |  |  |  |  |  | 07 |  |  |  |
|  | 08 |  |  | 10 |  | 10 |  | 08 |  |  | Fuse Designation Card |
|  | 09 |  |  |  |  |  |  | 09 |  |  |  |
|  | 10 |  |  | 11 |  | 11 |  | 10 |  |  |  |
|  | 11 |  |  |  |  |  |  | 11 |  |  |  |
|  | 12 |  |  | 12 |  | 12 |  | 12 |  |  |  |
|  | 13 |  |  |  |  |  |  | 13 |  |  |  |
|  | 14 |  |  | 13 |  | 13 |  | 14 |  |  |  |
|  | 15 |  |  |  |  |  |  | 15 |  |  |  |
|  | 16 |  |  | 14 |  | 14 |  | 16 |  |  |  |
|  | 17 |  |  |  |  |  |  | 17 |  |  |  |
|  | 18 |  |  | 15 |  | 15 |  | 18 |  |  |  |
|  | 19 |  |  |  |  |  |  | 19 |  |  |  |
|  | 20 |  |  | 16 |  | 16 |  | 20 |  |  |  |
|  |  |  |  | 17 |  | 17 |  |  |  |  |  |
|  |  |  |  | 18 |  | 18 |  |  |  |  |  |
|  |  |  |  | 19 |  | 19 |  |  |  |  |  |
|  |  |  |  | 20 |  | 20 |  |  |  |  |  |

Figure 9-6:  Typical Layout of BDFB Fuse Panels

Figure 9-7:  Typical Layout of 2 Load 600 Ampere BDFB

Figure 9-8:  Typical Layout of 4 Load 400 Ampere BDFB

Battery return bus bars for the 7’-0” BDFB should be mounted using figures 9-10 and 9-11 as typical.  Nine foot or 11’6” BDFBs should be mounted per the Qwest Engineer’s instructions, Qwest standard configurations, and Technical Publication 77351.

Figure 9-9:  Typical Return Bus Bar Mounting for a 7’ BDFB (View A-A)

Figure 9-10:  Typical Return Bus Bar Mounting for a 7’ BDFB (View B-B)

No loads may be added to any BDFB that has been EMBARGOED.

One or more of the following labels shall be on every BDFB:

Figure 9-11:  Load and Embargo Labels for BDFBs

Equipment shelves may receive their A and B feeds from separate power sources (e.g., two different BDFBs and/or PBDs) only when the power sources have a normal operating Voltage differential of less than 0.3 V as measured at the equipment being fed, and only when the power sources ultimately use the same battery chemistry (e.g. flooded lead acid).

Fuse Bays (FBs) or miscellaneous fuse panels are designed to provide a centralized location for switching or IOF equipment to obtain power of small loads.  The FBs are provided with power from a BDFB, Power Board, ringing plant, etc.

Input connections to miscellaneous fuse or breaker panels fed by a fuse or breaker greater than or equal to 50 Amps shall be two-hole lug design.

Older FBs were equipped from the bottom up with filtered supplies being located at the bottom and miscellaneous supplies directly above.  Voltages increase toward the top of the bay.

Loads shall not be parallel fused (the same exact load position fed from more than one fuse or breaker).  Parallel fusing violates NEC Article 240.8.

A new BDFB/BDCBB should be added when any of the following occurs:

- The existing BDFB/BDCBB has no remaining fuse positions on the A side, B side, or both

- The actual load on any one side (A or B) or panel of a BDFB/BDCBB exceeds 50% of the protector size feeding it

- The List 1 (average busy-hour, busy-season) drains of the served equipment exceed the capacity of the BDFB.  The capacity is based on the rating of the upstream breaker or fuse.  As an example, a BDFB panel fed by a 400 Ampere protection device has a nominal load limit of 200 Amperes on any one side (A or B) so that their total load does not exceed the 400 Amperes fuse capacity.  Every effort should be made to obtain the List 1 drains from the equipment suppliers in order to determine whether another BDFB is needed.  However, in cases where only the List 2 drain can be obtained, List 1 for toll/transport/IOF loads can be estimated as the List 2 drain divided by 2.5.

Any given secondary or tertiary protection device shall be smaller than its upstream primary or secondary protection device (it may be equal to it if it is a faster responding fuse).  The engineering supplier is responsible for proper sizing of protection devices and wiring them correctly (this is known as fuse coordination).

When a fuse has blown, fuse positions shall not have residual Voltage bled to the outputs from fuse panel alarm circuitry.

## 9.7	Bus Bar Labeling and Layouts

The following bus bars should be installed, labeled and laid out in accordance with requirements herein, Qwest Technical Publications 77350, 77351, 77355; and standard configurations (note that the positions of the bars is for illustrative example purposes only, and may be different in actual practice depending on the space and needs in the site.

Figure 9-12:  Example of Bus Bars (Term Bars) above a Battery Stand

Term bars above a battery stand are typically used for stands that will have more than one string.  When there are stands with individual strings, they may often be cabled directly to the plant, or to the chandelier.

Figure 9-13:  A Battery Return Bus Bar above a BDFB

Figure 9-14:  Chandelier Hot Side Main Terminal (Term) Bar

Depending on the size of the plant, the hot side of the chandelier may be multiple bars.  In some cases no chandelier is used, and the batteries (and rectifiers when they are in separate bays) are cabled directly to the plant (PBD) hot busses.

Figure 9-15:  Chandelier Return Side Bars

There may also be a separate return bar over the PBDs (cabled to the discharge side of the chandelier), while the chandelier is typically located over the battery stands.  In smaller plants, the return bar may even be internal.

Figure 9-16:  Example of a Remote Ground Window

Figure 9-17:  Example Main Return / Ground Window MGB Bar

The charge/discharge bar is often physically separated (but connected by cabling) from the return bar that is part of the isolated portion of the MGB.

Figure 9-18:  Example of Sandwiched Terminations

CONTENTS

Chapter and Section 	Page

10.	Ring, Tone and Cadence Plants	10-1

10.1	General	10-1

10.2	Ringing and Tone Systems Technical Requirements	10-1

10.3	Distribution	10-2

10.4	Ringing Plant Alarms and Troubles	10-2

# 10.	Ring, Tone and Cadence Plants

## 10.1	General

This unit is intended to provide general information regarding:

- Ringing systems currently in use in switching and transmission systems;

- The various call progress tones furnished by ringing plants.

- General information on ring plant sizing.

In Stored Program Control System (SPCS) offices, ringing, call procession tones, precision tones - Dual Tone Multi-Frequency (DTMF), dial tone, audible ringing tone, high tone and low tone) are provided by the switch.  A separate ringing plant must be provide for all non-switched services such as Foreign Exchange (FX), ring down, Interexchange Carrier (IEC or IXC) special ringing requirements, metallic facility, DLC that doesn’t provide its own ringing, etc.  This section describes the requirements for that separate ringing plant.  (All power equipment must have completed the Qwest product selection procedure.)

## 10.2	Ringing and Tone Systems Technical Requirements

Ringing signal in Qwest is 20 Hz.  Call progress tones, such as dial and busy tones for the switched subscribers also need to be provided.  In most cases, the equipment providing POTS service (switch and/or DLC) provides both the ringing and the necessary tones either on the card, shelf, or bay.  In other cases, it might provide the tones but not the ringing current.  When either ringing current and/or tones are not provided by a piece of equipment but are necessary, they are supplied by a residual bulk ring plant (if tones aren’t needed, the plant doesn’t need to be equipped with that capability).

Where practical, the bulk residual ringing supply should be installed in close proximity to the circuits that need it.  However, when those circuits are found all over the site, the residual ring plant is often located in the DC power room.

When bulk residual ringing or tone (sometimes provided by interrupters) supplies are provided, they must be provided in a redundant configuration.  Transfer to the reserve unit may be accomplished by use of a manual transfer switch and automatically when the online supply fails.

The ringing equipment shall operate within an input Voltage range of -44 to -59 VDC (or -21.4 to -28 for nominal -24 VDC sites).  The ungrounded supply lead(s) must be properly fused, and must have separate feeders for the regular and reserve units.

The input circuitry to any ringing generator shall consist of an input fuse and an input filter that prevents noise from being fed back from the generators to the batteries.

The ringing equipment shall have built-in protection against undervoltage, overcurrent, and overvoltage on both the input and output.

The ringing generator output Voltage level shall be regulated to a constant Voltage level (typically between 86 and 88 VAC superimposed on -48 or +48 VDC, or nominal ±105 VAC for longer loops).

The wave shape of the ringing generator output must be low in harmonic content.

The efficiency of a ringing generator shall be high at light loads.

It is permissible to operate ringing generators in parallel, or in a primary-secondary configuration.  Generator output power may also be increased by use of a power booster.

It is permissible to use the same ringing generator for both battery and ground-connected trip circuits, provide that an isolation transformer is used.

Precise tone generators must have a frequency stability of ±0.5%, THD of 1% or less, and output Voltage regulation to ±1.0 dB.

The Receiver Off Hook (ROH) generator shall be designed for fully automatic operation with permanent signal line systems.  The 2600, 2450, and 2060 Hz frequencies of the ROH generator shall be stable within ±2% over the input Voltage range, and output load range from no load to full load.  The 1400 Hz frequency shall be stable within ±0.5% over the same input and output Voltage range.  Harmonics in the output frequencies of the ROH generator shall be limited to a level of 26 dB down from the level of the fundamental frequencies.

All components of the ringing equipment shall be removable through front access.  The ringing equipment shall be modular.

During growth and additions, the delivery of power to the using systems shall be maintained.

All ringing equipment shall have a nameplate with a minimum of the supplier’s name, model and serial numbers, and manufacturing date.

Residual ring plants should be sized at a minimum of approximately 15 VA for every 100 circuits served.

## 10.3	Distribution

At least one distribution fuse shall be provided at a minimum.  A primary or split fuse panel may also be used.  The engineering supplier is responsible for proper fusing and sizing of ringing supply leads.

Protection devices (fuses or circuit breakers) being fed from a ringing plant shall NOT exceed the capacity of the plant by more than 25 percent.  An example would be that a 100 VA ring plant shall not have a fuse larger than 1.33 Amperes to protect the using equipment.  Load fuses shall be smaller than the plant output fuse.

All distribution from SPCS ringing and tone frames to non-SPCS equipment must be run within three feet of the ground window and have the return lead bonded to the main ground bus.  When a separate residual ringing supply is provided, all of these circuits must be moved to the separate supply, and the leads rerouted.

Ringing plant distribution fuses shall not be multipled (e.g., daisy-chained) between equipment bays for new feeds, although daisy chaining of ringing distribution within a bay is permissible.

## 10.4	Ringing Plant Alarms and Troubles

Alarms are required for all office ringing supplies.  Typical alarms required are major, minor, ring machine transfer, and interrupter transfer (when there are interrupters).  Alarm indications, such as major, minor, and transfer should be visual on the plant, with provisions for remote alarming (dry Form C or Form A contacts).  All alarm points shall be easily accessible for connection to a PSMC.

During normal operation, if a trouble condition should occur in the regular 20 Hz ringing generator, tone generator, or the interrupter, the load shall transfer to the reserve unit after a 2 second time delay.  A trouble lamp(s) shall light to indicate trouble and an alarm signal(s) shall be activated.  After the trouble has been cleared, that unit shall transfer back to normal operation by manual transfer only.  In addition, all the associated alarm lamps shall be extinguished.  If some element in the reserve side of the equipment fails without an earlier failure in the regular unit, a trouble lamp(s) shall light to indicate which output has failed, and an alarm(s) shall be activated.

CONTENTS

Chapter and Section 	Page

11.	Power Pedestals	 11-1

11.1	General	 11-1

11.2	Materials	 11-1

11.3	Technical Requirements	 11-2

# 11.	Power Pedestals

## 11.1	General

This unit covers power pedestals for use in the Outside Plant environment.  The power pedestal is the interface between commercial AC, the standby AC connection (portable genset hookup), and the Outside Plant enclosure (e.g., CEV, RT, etc.).

The power pedestal shall be designed to prevent personnel exposure to safety hazards.  The pedestal will be equipped with warning signs and guards, in agreement with UL requirements.  The pedestal shall be Listed.

Due to right-of-way, roads, etc., it is not always possible to place a power pedestal next to the RT(s) it is serving.  Although a power pedestal can theoretically be placed up to 1000 feet from the RT(s) it is serving, it is typically not economical to place the RT more than 150 feet from its power pedestal.  A new location or an expanded ROW for the RT should be considered if this maximum 150-foot distance is exceeded.  The distance rules for the power pedestal from the transformer are the same.

Each pedestal and/or framework shall have a visible nameplate with the following information: suppliers name, serial number, model number, manufacturing date, nominal input Voltage(s), number of phases, rated frequency, the output Voltage (if equipped with a transformer that makes it different from the input Voltage, both must be Listed), the rated full load current, and the available interrupt current rating of the pedestal.

The interrupt current rating of the pedestal and its breakers must exceed the available fault current available from the serving utility company transformer.

The pedestal shall not have any openings sufficient to allow rodents, snakes, or other animals to enter and/or make their home inside the pedestal.

The pedestal shall meet the service requirements of any electric utility in Qwest territory.  In practical terms, this means that different models of pedestals must be provided for different areas.

Pedestals (and all AC services to Qwest sites) should be equipped with Transient Voltage Surge Suppression (TVSS).  The suppression technology can be MOV, SAD, or MOV/SAD hybrid designs.  All TVSS units must be UL 1449 edition 2.5 Listed, tested to the appropriate ANSI/IEEE C62 series standard, and installed in compliance with Articles 280 and 285 of the NEC (this also applies to Central Office TVSS).

## 11.2	Materials

Circuit breakers should have their interrupt current rating specified.

Input breakers for the commercial AC and portable genset must be of the walking beam interlock type transfer system.

Both ring and ringless type meter sockets are used, depending on the requirements of the serving electric utility company.  In some cases, a particular power pedestal model may come with a meter socket.  In those cases where the pre-installed meter socket is not acceptable to the serving utility, the contracted electrician may remove it and replace it with one acceptable to the serving utility.  In other cases, the power pedestal does not come with a meter socket.  In those cases, the electrician must provide one acceptable to the local utility.

Some utilities require an external (or separately accessible) disconnect other than the meter socket itself.

## 11.3	Technical Requirements

The structural members of the power pedestal shall not carry or conduct load currents under normal operating circumstances.

All metal parts shall be grounded.  Metal surfaces shall be bare metal at the points where they bolt together for bonding purposes or connect to the grounding system.

The pedestal shall be capable of being mounted in one or more of the following configurations: on a concrete pad (self-supporting), on a pole, or in a NEMA 1A type cabinet.  In practical terms, these are usually separate models.

Service entrance conductors shall be run only in conduit, and the pedestal shall be capable of overhead or underground entrance.  If entrance is through the bottom of the enclosure, the supplier must provide a vented dead air space.  No equipment shall be mounted in this area.  The space must be a minimum of four and one half inches in depth.  The load conductors shall be run only underground, and in conduit.

The enclosure shall be lockable.

The enclosure shall be equipped with either a hinged door opening to a minimum of 160 degrees, or a removable front cover.

The commercial AC feed must not be accessible to the public from the meter back towards the source.  While most power pedestals have internal risers for the electric utility feeds to the meter socket, some utilities require these to be in a separate compartment (lockable by them), or external to the power pedestal.

The load center must have a minimum of six (and preferably at least twelve) positions, pre-equipped with one 15-Ampere breaker to be wired to a GFCI receptacle.  The GFCI receptacle will be mounted in the enclosure.

Visual alarm and status indications shall be provided by colored, illuminated devices mounted directly on the power pedestal.  A dedicated overcurrent device operating from the plant Voltage should be provided to power the visual alarms in the subsystem that indicate that the power to the status indication and alarm overcurrent devices have operated, or that power has been removed from the status indication and alarm or control system.  The device can be either a fuse or circuit breaker in the ungrounded supply lead.

CONTENTS

Chapter and Section 	Page

12.	Lighting	 12-1

12.1	Emergency	 12-1

12.2	Task	 12-1

Tables

12-1	Wire and Protector Sizing for -48 VDC Powered Lighting Circuits	12-3

# 12.	Lighting

## 12.1	Emergency

Emergency lighting (also sometimes called stumble lighting) is required by the NEC and Life Safety Codes (it must come on within 10 seconds of a power outage and last for 90 minutes) for egress from a building (stairwell lighting, main aisle lighting, exit signs, etc.).  (Illumination levels and other detailed information can be found in NFPA 101 and in NEC Article 700.)  It should be run off a contactor or sensor, or left on all of the time.  This egress lighting is most reliable if -48 VDC powered, but the installation of this type of lighting is the ultimate responsibility of the Qwest Real Estate department.

Battery pack lights are sometimes used for emergency egress lighting, but are not the best choice, especially when their batteries are not maintained.  The most reliable choice for emergency lighting is -48 VDC powered fluorescent ballasts.  The second-most reliable choice is AC lighting fed by an inverter powered from a -48 VDC plant.  A third choice could be "emergency/egress" ballasts with a built-in battery.  Wall-mounted, ”frog eye” style lights are the fourth common type of emergency egress lighting system.

DC emergency and stumble light fixtures shall be labeled to preclude use of the wrong bulbs and/or ballasts.

## 12.2	Task

Task lighting is not code required, but is required by Qwest for the following locations:

- Engine Room (task lights are not required for outdoor engine enclosures)

- Transfer System Switchgear

- Indoor Engine Control Panel

- Indoor AC Service Entrance

- Main DC Power Boards (especially above the controller)

This lighting is best if it can be run on a switched circuit with a contactor or sensor that will light it up during an AC outage even if the switch is off.  Other options are running off a standard light switch, or on continually.

The following methods can be used to provide this lighting:

Incandescent bulbs shall be -48 VDC types.  These older systems cannot usually be maintained due to the fact that the bulbs are no longer made and are very difficult to find.  There are both right and left-handed thread -48 VDC incandescent bulbs and fixtures.  Also used were positive or negative 130 VDC fixtures and bulbs (standard 120 VAC bulbs can be used in these systems, but system labeling for these and for right-handed thread -48 VDC incandescent systems is critical so that maintenance personnel know whether they are dealing with an AC or DC system).  These incandescent systems typically use a contactor that takes a non-essential AC source to hold the contacts open, but allow DC to flow when the AC is off.  These systems should be replaced with fluorescent fixtures at the next convenient opportunity.

Fluorescent ballasts for task lighting shall be -48 VDC types (as noted previously, these same ballasts could also be used for emergency/egress lighting).  There are several suppliers for these ballasts.  They can be used in existing fixtures with existing bulbs.  There are -48VDC input fluorescent ballasts that can be used in an always-on configuration, or in a switched circuit.  Note however, that with these ballasts in a switched circuit, they will not automatically re-power the lights in an AC Fail condition if the switch is turned off.  In addition, there are -48VDC inverter “ballasts” that do not power the tubes directly, but are instead wired in parallel with an AC input fluorescent ballast.  If wired correctly, these can be used in a switched circuit that will automatically power/light the fixture in the event of an AC failure, regardless of whether the switch is "off or on".

DC lighting can be fed from the nearest -48 VDC source (main Power Board, BDFB, or even miscellaneous fuse panels).  If feeding from the main Power Board or BDFB, it is permissible to run several fixtures in parallel off a single circuit (similar to AC lighting), following the provisions of the NEC.

Because of the low power drain of DC lighting fixture ballasts (typically 1-2 Amperes of -48 VDC current per fixture), and since we use the nearest DC source, and the minimum Voltage of the bulbs or ballasts is typically 30 VDC, Voltage drop will not normally be an issue.

The following wire and fuse or circuit breaker sizing guidelines might generally apply for -48 VDC lighting circuits.

Table 12-1 Wire and Protector Sizing for -48 VDC Lighting Circuits

| Number of Fixtures | Minimum Wire size (AWG) | Protection Device Size (Amperes) |
| --- | --- | --- |
| 1 | 14 | 5-15 |
| 2-3 | 14 | 10-15 |
| 4-5 | 14 | 15 |
| 6-7 | 12 | 20 |
| 8-10 | 10 | 30 |

Any circuit feeding more than three fixtures should be fed from a BDFB or main Power Board, not a miscellaneous fuse panel.

Although not required, these DC lighting circuits would generally be run in conduit.  This conduit cannot contain any AC circuit wires.  The DC wires cannot be white, red, blue, brown, orange, or yellow.  This will generally prevent accidental connection at junction boxes to the AC system.  A green wire ground shall also be run, in accordance with the NEC, and tied down to the ballast and/or bonded to any metallic fixture case it feeds.  Back at the fuse source, the green wire ground can then be tied to the frame.  Any conduit must be metallically bonded back to ground too, either with a bond to the green wire at the fixture case, or at the junction box, etc.  The size of this ground wire does not need to be any larger than the largest -48 VDC or return conductor run in the conduit.

If the site has a power inverter with spare capacity, regular AC lighting can be provided from it.  It can be switched or permanently on, or on a contactor, depending on whether it is emergency or task lighting.  (Each fixture uses 75-100 W/VA of inverter load.)  The fixture shall have a label visible from the floor identifying it as inverter fed.

If you have a site that has multiple engines in parallel, task lighting (but not emergency egress or stumble lighting) can be from the essential AC bus fed by these paralleled engines.

Standard low-level equipment lighting arrangements shall be installed per Qwest Technical Publication 77351 and Qwest Standard Configuration documents.

For external engine enclosures, task lighting (if provided at all) can be powered off of the engine start battery circuit only if it is on a timer switch so that it does not drain the battery.  DC leads should not be run from the building to perform this function or to provide emergency egress lighting for a walk-in enclosure due to the risk of bringing lightning back into the DC plant.  Inverter powered lighting is an option for outdoor engine enclosures for egress and/or task lighting, but the circuit must have a TVSS device at the point it enters/leaves the main building.

CONTENTS

Chapter and Section 	Page

13.	Standard TL1 Messages and Alarm Settings for Power	 13-1

13.1	General	 13-1

13.2	AIDs and Condition Types for Power Alarms	 13-2

13.3	“Reduced Character” and Overhead Bitstream TL1             Condition Types	 13-7

13.4	TL1 Query Messages for Power	 13-9

13.5	Analog Power Alarm Set Points (Thresholds)	 13-11

13.6	Typical Power Alarm and Monitor Points	 13-20

13.6.1	Typical PSMC-CL Points in Smaller Sites	13-21

13.6.2	Typical Central Office Power Alarm Points	13-23

13.7	Power SNMP Traps for DSL and Ethernet Locations	 13-26

CONTENTS (Continued)

Tables

13-1	AID for Power Alarms	13-3

13-2	Power Alarm Condition Types	13-5

13-3	“Reduced Character” and Overhead Bitstream TL1 Alarm             Condition Types	13-8

13-4	TL1 Query Messages for Power	13-9

13-5	Part 1A:  Alarm Thresholds on Analog Points — DC Voltage for Plants Floating from -52.0 to -52.8 VDC	13-12

13-5	Part 1B:  Alarm Thresholds on Analog Points — DC Voltage for Plants Floating from -53.8 to -55.3 VDC	13-14

13-5	Part 1C: Alarm Thresholds on Analog Points — DC Voltage for “Constant Current” Charging	13-14

13-5	Part 1D:  Alarm Thresholds on Analog Points — DC Voltage Set Points for Lithium-Based Batteries	13-15

13-5	Part 1E:  Alarm Thresholds on Analog Points — DC Voltage Set Points for Converter Plants and Engine Start Batteries	13-15

13-5	Part 2:  Temperature Compensation and Current Limiting	13-16

13-5	Part 3:  Alarm Thresholds on Analog Points — Temperatures	13-17

13-5	Part 4:  Alarm Thresholds on Analog Points — DC Current	13-18

13-5	Part 5:  Alarm Thresholds on Analog Points — AC Voltage	13-19

13-5	Part 6:  Alarm Thresholds on Analog Points — AC Current	13-20

13-5	Part 7:  Alarm Thresholds on Analog Points — Fuel Alarm Thresholds	13-20

13-6	Part 1A:  Typical Power Alarm and Monitoring Points for OSP Cabinets and Customer Premise	13-21

13-6	Part 1B:  Typical Power Alarm and Monitoring Points for CEVs, huts, CdOs (small COs without engines) and Radio Sites (PSMC-CL                  or PSMC)	13-22

13-6	Part 2:  Typical Power Alarms and Monitoring for COs with Engines	13-24

13-7	SNMP Power Alarm Messages used in Qwest	13-26

# 13.	Standard TL1 Messages and Alarm Settings for Power

## 13.1	General

The attached information is the standards for Qwest for Power messaging over PSMCs, using the X.25or IP packet protocol with TL1 command language.  It is to be used primarily for configuring, alarming, and interpreting messages interfaced to NMA in LNS (NNS monitors are generally not directly interfaced to NMA, and standards for NNS alarm messaging are found in PRD-00690).

There are several parts to this chapter.  Sections 13.2 and 13.3 and Tables 13-1 through 13-3 explain the use of the AID and Condition Type fields (messages from Tables 13-1 and 13-2 also are used to database binary alarms in NMA that come in through Dantel devices or other devices that communicate via e-telemetry).  Section 13.4 and Table 13-4 define the TL1 queries that may be performed on X.25 and IP-compatible Power System Monitor/Controllers (PSMCs) to extract useful information from them.  Section 13.5 and Table 13-5 (with its various sub-parts) defines the threshold settings for binary alarms derived from analog readings.  Section 13.6 and Table 13-6 provide a few examples of typical standard power messages.  In Qwest LNS, most power alarms report into NMA.  However DSL and Ethernet services report alarms via SNMP.  Section 13.7 covers some of the standard power messages found in Qwest SNMP networks.

Power and environmental alarms make their way to NMA over one of four different transmission media.  These media are listed below in order of preference (for example, Qwest prefers e-telemetry transmission of power and environmental alarms over switch transmission).  Alarms should not be sent through more than one of these mediums (except for backup generic majors and minors) due to the confusion multiple alarming causes for the surveillance technicians.  Preference is based on the ease of NMA routing and/or analysis allowed by the particular media.

- TL1 on an X.25 or IP circuit from a Power Monitor (PSMC) with backup major, minor and watchdog alarms through an e-telemetry or switch medium (environmental alarms in a CO should not generally use a PSMC, except for those specifically related to power, such as a battery room temperature)

- E-telemetry (e.g., Dantel, etc.), or similar modern alarm systems that report e-telemetry (binary alarms) via an IP circuit

- X.25 overhead bitstream from Remote Terminal (RT) locations

- Through the switch scan points

Binary alarms connected to any of the above devices may be connected as closed on alarm (NO), or open on alarm (NC).  Either configuration is acceptable for power and environmental alarms.

Most alarms are typically set up as closed on alarm (NO).  However, critical alarms should probably be connected to open on alarm (NC).  This setup (of alarming on an open condition) is also known as “guarded”.  This refers to the fact that if the wiring is inadvertently cut or disconnected, or contacts get dirty, an alarm will be brought in.  If alarms are connected in the “guarded” state, it is preferable that the reversal of the point be done on the alarm-monitoring device rather than in NMA.  If the reversal is done in NMA, it can cause problems for both field and center technicians by causing red lights, or bit sets (which normally mean alarmed conditions to these technicians) when there actually is no alarm.

## 13.2	AIDs and Condition Types for Power Alarms

The AID provides a "gross" definition of the equipment involved.  An "n" associated with an AID indicates more than one entity of that type.  The "n" will always be a number.

The second column in the AID table (normally called the sub-AID) on the following pages provides a detailed identification of the hardware involved in the message.  Every message will use the first column.  However, the second column will not be used for every alarm condition.  An "m" associated with the second column indicates more than one entity of that type.  The second column may or may not have an associated "m".  The "m" may be numeric, alpha, or alphanumeric.  For those messages with the "m", it does not have to be there (this is especially true for generic plant alarms, such as a plant rectifier fail alarm).

As examples of messages, N48B1RECT4 refers to rectifier 4 in the negative 48-Volt battery plant #1; and N48B1RECT would be the overall AID for the generic plant rectifier alarm.

- CONDITION TYPE (CONDTYPE) uniquely defines the condition or trouble to be provided to NMA from the alarm reporting device.  The CONDTYPE field is completely independent of the AID field.

In order to obtain a full description of the problem associated with a particular NMA message, the AID and CONDTYPE must be provided.  For example, a CONDTYPE of FAIL associated with an AID of N48B1RECT4 would indicate that rectifier 4 in the negative 48-Volt battery plant #1 failed.

N48B1RECT4 FAIL

Alarms are classified as minor (MN), major (MJ), and critical (CR) depending on the criticality of the alarm, and the time allowed before action must be taken.

For power monitors capable of TL1 over X.25 or IP, a generic TL1 template should be generated in NMA against the monitor at a site (the TID of the monitor).  This template generates numerous NMA AID entities for that TID.  If the AIDs programmed into the monitor match the AID entities of the template that is generated against the TID no more NMA programming needs to be done.  However, each alarm must still be tested to ensure electrical and database continuity, as it is impossible to make the template large enough to be all inclusive of every type of possible power alarm.  So, if an alarm is tested after the template is generated, and a ticket is not created, a specific entity for that alarm must be created, or the AID in the monitor must be changed to match one of the template AIDs.  Condition types are not generated in the NMA database.  These TL1 condition types pass straight through from the monitor on the X.25 or IP link as pure ASCII text.

Table 13-1 AID for Power Alarms (page 1 of 2)

| AID + sub-AID | Description of AID |
| --- | --- |
| BATTERY PLANT |
| P130Bn |  | positive 130 Volt battery plant #n |
| N130Bn |  | negative 130 Volt battery plant #n |
| N48Bn |  | negative 48 Volt battery plant #n |
| P24N48n |  | positive 24 and negative 48 Volt battery plant |
| P24Bn |  | positive 24 Volt battery plant #n |
| N24Bn |  | negative 24 Volt battery plant #n |
| PSMCn |  | power systems monitor/controller |
| COM |  | internal PSMC message |
|  | LVD | low Voltage disconnect unit or contactor |
|  | MPROC | micro processor |
|  | PWRSUPPLY | internal power supply or feeding power supply |
|  | ROOM | ambient power room temperature |
|  | RPMm | Remote monitoring module for a PSMC |
|  | SHUNTm | shunt or sub-shunt "m", or shunt-monitoring board |
|  | TIMER | elapsed timer |
|  | BATmLO | a cell in the lower tier of battery string "m" |
|  | BATLIm | Li-based battery |
|  | BATm | battery string "m" |
|  | BATmHn | battery half string Voltage in string "m", "n"th half of string |
|  | BATmM | battery midpoint Voltage for string "m" |
|  | BATmPC | pilot cell in string "m" |
|  | BATmQn | quarter string Voltage in string "m", "n"th quarter of string |
|  | BATmUP | a cell in the upper tier of battery string "m" |
|  | BMS | battery temperature compensation device |
|  | ABS | fuse feeding alarm relays |
|  | CHARGE | charge fuse (input fuse) |
|  | CNTRLm | control fuse, breaker or relay "m" |
|  | DISTm | distribution (discharge) fuse/breaker "m" |
|  | REG | Voltage regulator power supply or regulator fuse |
|  | RECTm | rectifier "m" |

Table 13-1 AID for Power Alarms (page 2 of 2)

| AID + sub-AID | Description of AID |
| --- | --- |
| CONVERTER PLANT |
| P130Cn |  | positive 130 Volt converter plant #n |
| N130Cn |  | negative 130 Volt converter plant #n |
| PN130C |  | positive & negative 130 Volt converter plant #n |
| P48Cn |  | positive 48 Volt converter plant #n |
| N48Cn |  | negative 48 Volt converter plant #n |
| P24Cn |  | positive 24 Volt converter plant #n |
| N24Cn |  | negative 24 Volt converter plant #n |
|  | ABS | fuse feeding alarm relays |
|  | CONVm | converter "m" in plant #n |
|  | DIST | distribution fuse/breaker for plant #n |
| INVERTER PLANT |
| 1PHINVn |  | single-phase inverter plant #n |
| 3PHINVn |  | 3-phase inverter plant #n |
|  | TRNSW | transfer switch in _-phase inverter #n |
|  | DIST | distribution fuse/breaker for _-phase inverter #n |
| UPS |
| 1PHUPSn |  | single-phase UPS plant #n |
| 3PHUPSn |  | 3-phase UPS plant #n |
|  | BATCHGm | battery charger "m" in _-phase UPS #n |
|  | BATm | battery string "m" in _-phase UPS #n |
|  | INVm | inverter "m" in _-phase UPS #n |
|  | TRNSWm | transfer switch "m" in _-phase UPS #n |
| RING PLANTS |
| RNGn |  | ringing generator (plant) #n |
|  | FUSEm | ringing generator fuse "m" |
|  | RGENm | ringing generator "m" in ring plant #n |
|  | INTERm | ringing interrupter "m" in ring plant #n |
| STANDBY ENGINE-ALTERNATORS |
| ENGALTn |  | stand-by engine/alternator #n |
|  | FUELPRES | fuel pressure |
|  | BATCHG | start battery charger for standby engine #n |
|  | BATENGm | start battery string "m" for standby engine #n |
|  | COOLANT | standby engine coolant |
|  | CURNTm | input AC phase "m" current |
|  | DAYFUEL | day tank of standby engine #n |
|  | FAIL | optionally used for engine failure |
|  | FAN | fan for standby engine #n |
|  | KWm | power produced by phase “m”, or total engine power |
|  | MAINFUEL | main fuel tank of standby engine #n |
|  | OIL | oil level |
|  | OILPRESS | oil pressure for standby engine #n |
|  | PHASEm | AC phase from engine/alternator |
|  | ROOM | ambient engine room temperature |
|  | TRNSWm | transfer switch "m" operated |
|  | VOLTm | engine output AC phase "m" Voltage |
| COMMERCIAL OR STANDBY AC |
| COMACn |  | commercial AC service entrance #n |
| ACINn |  | AC measured on load side of transfer switch. #n (essential AC) |
|  | CURNTm | input or output AC phase "m" current |
|  | KWm | power produced by phase “m”, or total power |
|  | PHASEm | AC phase |
|  | TRNSWm | input AC transfer switch "m" |
|  | VOLTm | input AC phase "m" Voltage |

Table 13-2 Power Alarm Condition Types (page 1 of 2)

| CONDTYPE | CR, MJ, or MN | Description of Condition Type |
| --- | --- | --- |
| ALARM_CUTOFF | MN | alarm cutoff — can also indicated by adding " _ACO" to other condition types |
| BYPASS | MN | inverter, or UPS bypass mode |
| CAPACITY_EXCEEDED | MN | near or exceeding capacity of plant, rectifier, etc. |
| COML_AC_FAIL | MJ | commercial AC failure |
| CRANK_FAIL | MJ | engine has cranked too much and cannot start |
| CRITICAL | CR | a critical power alm. (e.g., very low Voltage, temperature differential) |
| CTLLR_OK | — | internal message (used with a watchdog) |
| DIFFERENTIAL_TEMP | MJ/CR | high or low differential temperature between batteries and ambient — criticality depends on threshold (see section of this document dealing with that issue) |
| DISCONNECT | MJ/MN | any disconnect operated (minor if there is redundancy) |
| ELAPSED | MN | an alarm has timed out (elapsed) |
| EMERGENCY_STOP | MJ | standby engine emergency stop, or any other emergency stop |
| EMG_STOP_BUTTON | MJ | emergency stop button has been operated |
| FAIL | MN/MJ | any equipment or plant failure — minor for individual rectifiers, ringers, or converters, major for multiples of these |
| FAIL_PARALLEL | MJ | engine-alternators failed to parallel |
| FAN | MJ | rectifier, engine, or UPS fan fail alarm |
| FUEL_LEAK | MJ | any fuel tank leak |
| FUEL_SYS_TRBL | MJ | alarm from fuel system monitor. |
| FUSE/BRKR_OPERATE | MJ/MN | any fuse or breaker operation — generally major for main power board distribution fuses unless otherwise specified |
| GROUND_FAULT | MJ | ground fault has been detected and AC possibly disconnected at engine or HSP |
| HIGH | MN/MJ | any high fluid level or pressure |
| HIGH_FLOAT_AMPS | MN | float current is higher than it should be; indicating batteries near end-of-life |
| HIGH_FREQUENCY | MJ | UPS or standby engine high frequency |
| HIGH_TEMPERATURE | MJ | any high temperature (environment or equipment) — critical for some battery temperatures (see threshold section of this document), and major for everything else |
| HIGH_VOLTAGE | MJ | any high Voltage, AC or DC — criticality depends on threshold (see section 9 of this document) — assume major |
| HIGH_VOLTAGE_HVSD | MJ | the rectifier(s) have shut down on high Voltage |
| IMBALANCE | MN | current is imbalanced between phases, battery strings, or rectifiers |
| INPUT_FAIL | MJ | any AC or DC input fail |
| LOCKOUT | MJ | input or output locked out (turned off or failed) |
| LOW | MJ | any low fluid level or pressure |
| LOW_TEMPERATURE | MJ | any low temperature, including engine block heater fail |
| LOW_VOLTAGE | MJ | any low Voltage (e.g., low float, or battery on discharge) |
| LO_VOLT_DISCONNECT | CR | plant, battery, or load disconnect on low Voltage |
| MAJOR | MJ | any generic major alarm from the power plant |
| MAJOR_CRITICAL | MJ | any power major or critical — used when not enough points |

Table 13-2 Power Alarm Condition Types (page 2 of 2)

| CONDTYPE | CR, MJ, or MN | Description of Condition Type |
| --- | --- | --- |
| MICROPROC_FAIL | MN | the microprocessor in the PSMC or power plant has failed |
| MINOR | MN | any generic minor alarm from the power plant |
| MULTIPLE_ALARMS | MJ | used when PSMC has to upgrade an alarm from minor to major |
| NORMAL | MN | any normal position (e.g., transfer switch) |
| OFF_(NORMAL) | MN | equipment normally off |
| OFF_NORMAL | MJ/MN | equipment not in a "normal" functioning condition |
| OPERATE | MN/MJ | a switch or other device has operated — criticality will depend on the alarm. If this is simply a status alarm, it is a minor. It is a major for all other cases |
| OVERCURRENT | MJ | excessive current on distribution, rectifiers, etc. |
| OVERRIDE | MN | the override of any function |
| OVERSPEED | MJ | engine overspeed |
| PROPER_OPERATION | MN | proper operation for any equipment |
| RECHARGE | MN | indicates batteries are recharging |
| RELAY_OPERATE | MN | any relay has operated |
| RESTART | MN | equipment has restarted |
| RESET | MN | any reset condition |
| RESTORE | MN | any restored condition |
| REVERSE_POWER | MJ | alternator output power is reversed |
| SEQUENCE | MN | rectifiers are sequencing back on line to avoid engine overload |
| SHUNT_FAIL | MN | shunt board/communications failure |
| STBY_ENG_FAIL | MJ | standby engine/alternator has failed |
| STBY_ENG_RUN | MN | standby engine/alternator running |
| SURGE_ARRESTOR | MJ | commercial AC high Voltage or spike protector problem |
| TIMER | MN | sequence, engine, etc., timer or other type of timer problem or timeout |
| TRANSFER | MN | any transfer (ring, inverter, etc.) |
| UNABLE_EQUALIZE | MN | plant Voltage controller unable to switch to equalize Voltage |
| UNABLE_FLOAT | MJ | plant Voltage controller unable to switch to float Voltage |
| VERY_LOW_VOLTAGE | CR | very low Voltage — AC or DC |
| VOLTAGE_OUT_OF_LIMIT | MJ | use when alarming device can't distinguish high and low |
| WATCHDOG | CR | the PSMC is not working |

## 13.3	“Reduced Character” and Overhead Bitstream TL1 Condition Types

Some smaller battery monitors are not capable of holding all of the characters described in Table 2 above.  Some fiber multiplexers, that carry power and environmental alarm messages on their X.25 overhead bitstream, are sometimes limited to 10 characters for the TL1 condition type (often referred to in manufacturer or Telcordia (Bellcore) documentation as the ALMTYPE).  This TL1 condition type for these messages must totally describe the event within the 10-character limit.  Most muxes also have a miscellaneous minimum 40-character text field that can be seen by browsing the mux or sending an RTRV-ATTR-ENV or RTRV-ALM-ENV TL1 command.  The following shortened messages may be used in place of the messages of Table 13-2.  If a message is not found here, that means the message of Table 13-2 is short enough.  In some muxes, the ALMTYPE 10-character message is limited to the standard Telcordia (Bellcore) set (those where the description is in quotation marks), but the applicable power messages from the standard Telcordia (Bellcore) set are among the messages in the table below:

Table 13-3 “Reduced Character” and Overhead Bitstream TL1 Alarm Condition Types

| CONDTYPE (ALMTYPE) | CR, MJ, or MN NTFCNCODE | Description of Condition Type (some of this may be used in the 40-character ALMMSG field) |
| --- | --- | --- |
| BATDSCHRG | MJ | "battery discharging" |
| LOVOLTAGE |  | "low battery Voltage" |
| LWBATVG |  |  |
| RECTLO |  | "rectifier low Voltage" |
| BATMIDVOLT | MN/MJ | battery string midpoint Voltage imbalance (see Table 13-5) |
| BATTDISC | MJ | battery disconnect breaker manually or automatically operated |
| BATTERY | MJ | "battery failure" |
| BATTTEMP | MJ | high battery temperature |
| CKTBRKR | MJ | any breaker operated |
| COMLACFAIL | MJ | "commercial power failure" |
| POWER |  |  |
| CPMAJOR | MJ | “centralized power plant major alarm” |
| N48B1MJ | MJ |  |
| CPMINOR | MN | “centralized power plant minor alarm” |
| N48B1CR | CR |  |
| DIFFTEMP | CR | high differential temperature between batteries and ambient |
| ENGINE | MJ | “engine failure” or “generator failure” |
| GEN |  |  |
| ENGOPRG | MN | “engine operating”/running |
| DISTFUSE | MJ | "fuse failure" |
| FUSE |  |  |
| HIFLOATAMP | MN | float current is higher than it should be; indicating battery end-of-life |
| HI-LOVOLT | MJ | high or low DC plant Voltage |
| HIVOLTAGE | MJ | high DC plant Voltage |
| RECTHI |  | "high rectifier Voltage" |
| LIGHTNING | MJ | TVSS surge arrestor alarm |
| LOWFUEL | MJ | “low fuel” alarm for the tank feeding the engine |
| LWFUEL |  |  |
| LVDDISC | CR | low Voltage disconnect switch operated |
| LVDFAIL | CR | low Voltage disconnect device has failed |
| N48B1MJCR | MJ | power major or critical – used when not enough points |
| N48B1MN | MN | any power minor alarm combined on this point |
| OVERCURNT | MN | plant “load exceeds” 80-100% of n-1 “rectifier capacity” |
| RECTCAP |  |  |
| PWR-48 | MN/MJ/CR | "48 Volt power supply fail" |
| RECT | MN/MJ | "rectifier failure" |
| RECTFAIL |  |  |
| RINGFUSE | MJ | ringing distribution fuse operated |
| RINGMN | MN | ringing plant generic minor (e.g., one ring generator failed, etc.) |
| RINGMJ | MJ | ringing plant generic major (e.g., both ringers failed, etc.) |
| WATCHDOG | MJ | battery monitor or power monitor failure |
| VHILOVOLT | CR | very high or very low Voltage |

## 13.4	TL1 Query Messages for Power

A power monitor or a mux equipped for X.25or IP communication may receive messages, as well as send the SIDs, AIDs, and condition types defined earlier.  The messages that these machines may receive (along with a couple of “report out” messages) are defined below.  Each machine, depending on the manufacturer, will not accept all of the messages listed below, only the ones that have been programmed into that machine's hardware and software (the minimum required power monitor messages have been marked with an asterisk).  The message shown below is not the complete message; most messages include the AID and other commands defining what the user is looking for.  See the Telcordia (Bellcore) GRs-811, 833, and associated documents (or the manuals for the monitor) for the correct and complete formats.

Table 13-4 TL1 Query Messages for Power (page 1 of 2)

| MESSAGE | EXPLANATION |
| --- | --- |
| ACT-USER * | a logon (not required if software configured correctly) |
| ALW-MSG-ALL | not necessary if the software doesn't restrict messages |
| ALW-MSG-EQPT | allow an individual alarm message to be sent |
| CANC-USER * | a logoff if ACT-USER was used |
| DLT-SECU-USER | remove a TL1 user |
| ED-DAT | edit date and/or time |
| ED-SECU-USER | modify a TL1 user's privileges, passwords, etc. |
| ENT-SECU-USER | add a TL1 user |
| INH-MSG-EQPT | prevent an alarm message from being sent |
| INIT-REG-EQPT | initialize register: turn statistics on/off, erase highs and lows |
| INIT-SYS | reboots the system |
| MEAS-CUR | measure current |

Table 13-4 TL1 Query Messages for Power (page 2 of 2)

| MESSAGE | EXPLANATION |
| --- | --- |
| MEAS-VG | measure Voltage |
| OPR-ACO-ALL | masks or removes all alarms |
| OPR-ACO-EQPT | operate alarm cutoff for individual alarm |
| OPR-EXT-CONT | operates a control relay (e.g., shutdown rectifier) |
| RLS-EXT-CONT | releases the operated control relay (e.g., turn rectifier back on) |
| RTRV-ALM-ALL * | retrieves all alarms |
| RTRV-ALM-ENV | retrieve alarm information from "environmental" alarms info for a specific overhead bitstream housekeeping alarm |
| RTRV-ALM-EQPT * | retrieve a specific alarm or all active alarms, depending on the PSMC |
| RTRV-ATTR | retrieve alarm security (major, minor, etc.) |
| RTRV-ATTR-ENV | Retrieve information for overhead bitstream alarm points |
| RTRV-ATTR-EQPT | retrieve alarm security (major, minor, etc.) for a specific alarm |
| RTRV-EQPT * | retrieves the settings for a specific AID (channel) |
| RTRV-EXT-CONT | retrieve the state of an external control relay or contact |
| RTRV-HDR * | retrieves header info on site and monitor |
| RTRV-MMREPT | reports analog readings for a particular AID |
| RTRV-PM-ALL | retrieves readings, histories, and statistics for all channels |
| RTRV-PM-EQPT | retrieve current readings, statistics, or highs and lows |
| RTRV-SECU-USER | retrieve a list of authorized TL1 users |
| RTRV-TH-EQPT | retrieve alarm thresholds for a specific alarm |
| SET-ACO-EQPT | set up the alarm cutoff mode |
| SET-ATTR-ENV | Change the classification and messages of an overhead alarm |
| SET-ATTR-EQPT | change the classification (major, minor, etc.) of an alarm |
| SET-SID | set the office name or name of the alarm device |
| SET-TH-EQPT | set the thresholds for a specific alarm |
| REPORT MESSAGES (these precede the actual alarm message to NMA) |
| REPT^ALM^ENV | cause an environmental alarm and verify output |
| REPT^ALM^EQPT * | cause a power alarm and verify output |

## 13.5	Analog Power Alarm Set Points (Thresholds)

Analog points are derived from reading actual Voltage or current levels within the system and delivering alarms based on the analog levels or combinations of various analog levels and binary states.

Analog points are based on temperature, Voltage, current, or a combination of analog and binary information.  The following tables describe the values that should be associated with the various analog levels.

In many cases, both minor and major alarm thresholds are listed for each type of alarm.  For Voltage and temperature set-points cases, typically only the major alarm is required and the minor alarm is optional if the monitor type allows it, and/or there are enough spare points.  For current capacity exceeded alarms, it is preferable to have both major and minor thresholds, but as a bare minimum, the minor should be provisioned.

The values in Parts 1A through 1C of Table 13-5 are based on single cell lead-acid Voltages and 24 cell (-48 V) battery strings unless otherwise specified.  For other strings (e.g., ±130 V, or ±24 V), simply multiply the single cell numbers by the number of cells to obtain the correct string thresholds.

This document (and others) reflects a transition from a traditional flooded lead-acid float Voltage of -2.17 to -2.20 Volts per flooded cell (as recommended by flooded battery manufacturers) in order to provide more reliable batteries.  The further stipulation is that all new -48 V battery plants have 24 batteries per string, providing a float Voltage of approximately -52.80 V for flooded strings.  Sites that won’t function with a float Voltage of -2.20 V/cell (some older plants cannot easily have the float Voltage raised to -52.80 V due to HVSD settings, etc.); or that have lead antimony batteries; must be configured at the traditional -2.17 V/cell.  For lead-calcium batteries that cannot be raised due to alarm or HVSD settings, perhaps the float can be raised part of the way (for example, -52.50).  This is better for these batteries than the traditional -52.08.

Boost or equalize Voltage should only be used in rare cases to quickly recover battery capacity, it should be closely monitored to ensure we don't stay in boost mode too long).  Voltages should generally be set at about -54 V for a -48 V flooded cell plant (don't boost or equalize VRLA cells as a general rule), and if there are associated high Voltage alarms for the boost mode, set them 1 V higher (-55 V).

Table 13-5 Alarm Thresholds on Analog Points Part 1A:  DC Voltage for Plants Floating from -52.0 to -52.8 VDC

| AID or | CONDTYPE | MJ, MN | NOTES | THRESHOLDS |
| --- | --- | --- | --- | --- |
| SUB-AID |  | or CR |  | LOWER | UPPER |
| BATmPC | LOW_VOLTAGE or HIGH_ VOLTAGE | MINOR | CELL float VOLTAGE normally -2.20 V/cell (-2.17 V/cell under certain conditions) | ±0.05 V/cell (±0.03) from the nominal float of the pilot cell |
|  | or VOLTAGE_OUT_ OF_LIMIT | MAJOR | (if only one alarm is possible, Major is preferred to Minor) | ±0.07 V/cell (±0.04) from the nominal float of the pilot cell |
| N48B1 | LOW_VOLTAGE or HIGH_ VOLTAGE or VOLTAGE_OUT | MAJOR | plant float VOLTAGE -52.80 V plant float VOLTAGE -52.08 V | -50.1 -50.1 | -53.8 -53.1 |
|  | _OF_LIMIT or VERY_LOW_ VOLTAGE | CRIT. |  | -46.5 | -54.5 |
|  | HIGH_VOLTAGE_ HVSD | CRIT. |  | -54.0 (restart) | -56.0 |
| LVD | DISCONNECT | CRIT. | at the plant at the equipment (per mfg; or) | -43.25 -42.0 | -44.0 reconnect |
| BATmM | LOW_VOLTAGE or HIGH_ VOLTAGE | MINOR | (midpoint Voltage should be near -26.4 or -26.04) | -25.6 -25.3 | -27.2 -26.8 |
|  | or VOLTAGE_OUT_ OF_LIMIT | MAJOR |  | -24.8 -24.5 | -28 -27.7 |
| BATmH | VOLTAGE_OUT_ | MINOR | differential Voltage when comparing |  | 0.8 |
|  | OF_LIMIT | MAJOR | the two halves of a battery string |  | 1.6 |

These points can be set at the PSMC, the conventional DC Plant Controller, and/or the Rectifiers, depending on the manufacturer and model.  When the set points can be set in multiple places, the PSMC takes first priority (uses the levels given above), the Plant Controller second priority, and the Rectifiers final priority.  In these cases, each successive priority level should be set approximately 0.5 V above or below (depending on whether it is a high or low Voltage threshold, respectively) the previous value.  For example, if I set the PSMC Low Voltage at –50.1 V, I can set the DC Plant Controller Low Voltage at –49.6 V, and the Rectifier Low Voltage at –49.1 V.

The exception to this rule is for HVSD.  In the case of HVSD, the controller should have the lowest Voltage setting (-56 V, as shown above), and the rectifiers should be set at –56.5 V.  To help ensure that only offending rectifiers stay off, you may need to turn off load sharing in switch mode plants, and ensure that the plant rectifier restart circuit works.  If the switch mode rectifier plant is not capable of working without load sharing on, then it is best to set the rectifiers to the lower HVSD setting (if there are settings for both the rectifiers and controller).  Generally, PSMCs (unless an integral part of the Plant Controller) are not wired for control features (per Chapter 8), so HVSD would not be set on them (or if it is set, it would be the last level of defense — e.g., at –57 V).

It is generally not necessary to dual wire the same alarms (although backup major and minor alarms through a separate reporting device are encouraged).  For example, if each rectifier fail is directly wired to the PSMC, the rectifier minor from the plant controller is probably not necessary.

Very Low Voltage alarms (the “critical” low Voltage described above) are discouraged due to the confusion they introduce to those who monitor alarms when they are incorrectly set (those who monitor alarms at Qwest have the importance of the regular low Voltage alarm impressed upon them).  However, if a very low Voltage alarm is wired out or set to report an alarm, its threshold should be set at the -46.5 V level shown above.

VRLA Batteries less than a year old are still forming and equalizing in Voltage, so in that timeframe, they may be out of the pilot cell limits listed in the following table (it may be necessary need to set them wider initially).

Most of the Voltages in the following table are based on a premise of a float Voltage of -2.27 Volts per cell for the VRLA batteries, and that a 48 Volt battery string is equipped with 24 batteries (a float Voltage of -54.4 Volts).  Some VRLA strings are equipped with 23 cells because of a misassumption that some older equipment could not handle the -54.4 float Voltage (this fact is reflected in the table).

When Temperature Compensation is used, the pilot cell low Voltage alarm should be set at -2.15 Volts per cell for typical VRLA batteries (multiply this value by the number of cells to get the proper value for 4, 6, and 12 Volt batteries).  Similar settings may be needed for pilot cell high Voltage alarms when temperature compensation at low temperatures raises the Voltage

Low Voltage disconnects are generally discouraged (because they are usually designed to protect the batteries, but fail when they’re not supposed to, jeopardizing the critical loads) unless required by the manufacturer of the served equipment.  If used, they should generally be in series with only the batteries; and not directly in series with the load (unless required by an equipment manufacturer).

Table 13-5 Alarm Thresholds on Analog Points                 Part 1B:  DC Voltage for Plants Floating from -53.8 to -55.2 VDC

| AID or SUB-AID | CONDTYPE | MJ, MN or CR | NOTES | THRESHOLDS |
| --- | --- | --- | --- | --- |
|  |  |  |  | LOWER | UPPER |
| BATmPC or | LOW_VOLTAGE or HIGH_VOLTAGE | MINOR | normal CELL float VOLTAGE -2.25 to -2.27 V/cell at 77 degrees F | ±0.07 V/2 V cell (±0.10 V/4 V batt, ±0.15 V/6 V batt or ±0.25 V/12 V battery) from the nominal float of the pilot |
| BATmQn (quarter Voltages for 12 V batteries only) | or VOLTAGE_OUT_OF _LIMIT | MAJOR | (if only one alarm possible, Major is preferred to Minor) | ±0.13 V/2 V cell (±0.20 V/4 V batt, ±0.30 V/6 V batt or ±0.50 V/12 V battery) from the nominal float of the pilot |
| N48B1 | LOW_VOLTAGE or HIGH_VOLTAGE | MAJOR |  | -51.5 -49.4 | -56.5 -54.4 |
|  | or VOLTAGE_OUT _OF_LIMIT | CRIT. | plant float VOLTAGE -54.4 V plant float -52.2 V (23 cell string) | -46.5 | -57.0 -55.0 |
|  | HIGH_VOLTAGE_ HVSD | CRIT. |  | -56.1 (restart) | -57.5 -56.0 |
| LVD | DISCONNECT | CRIT. | at the plant at the equipment (per mfg; or) | -43.25 -42.0 | -44.0 reconnect |
| BATmM | LOW_VOLTAGE or HIGH_VOLTAGE | MINOR | midpoint measured between cells 12 | -26.2 | -28.2 |
|  | or VOLTAGE_OUT _OF_LIMIT | MAJOR | & 13 on a 23 cell string | -25.6 | -28.8 |
| BATmH | VOLTAGE_OUT_ | MINOR | differential Voltage when comparing the two halves of a battery string |  | 1.0 |
|  | OF_LIMIT | MAJOR |  |  | 1.6 |

Table 13-5 Alarm Thresholds on Analog Points Part 1C:  DC Voltage for “Constant Current” Charging

| AID or | CONDTYPE | ALARM | NOTES | THRESHOLDS |
| --- | --- | --- | --- | --- |
| SUB-AID |  |  |  | LOWER | UPPER |
| BATmQn | LOW_VOLTAGE or HIGH_VOLTAGE | MAJOR | CELL float VOLTAGE normally near -2.33 V/cell (-14.0 V/12 V battery) | -13.0 | -15.2 |
| N48B1 | LOW_VOLTAGE or HIGH_VOLTAGE | MAJOR | plant “float” VOLTAGE varies around -56.0 V | -52.5 | -59.5 |
|  | or VOLTAGE_OUT_OF _LIMIT | CRIT. |  | -46.5 | -60.5 |
| BATmM or BATmH | LOW_VOLTAGE or HIGH_VOLTAGE | MINOR |  | (0.8 V from ½ of the string Voltage |
|  | or VOLTAGE_OUT_OF _LIMIT | MAJOR |  | (1.6 V from ½ of the string Voltage |

Gates/Hawker 6-packs have a higher specific gravity, and therefore, a higher float Voltage than standard VRLA batteries.  Some plants designed for use with these batteries are not capable of being Voltage adjusted manually (e.g. AT&T/Lucent 3A, 3B, and J1C182Bx), but the chargers will fluctuate the Voltage greatly.  “Float” Voltages as low as -52.5, and as high as -59.5 are not abnormal, depending on the state of charge of the battery, in order to maintain a constant current to the battery.  In these cases, thresholds should be set at the levels of the preceding table.  Because of the variation in battery float Voltage, it may be wiser to alarm rectifier (as opposed to battery charger) Voltages in these plants (either at the levels of Parts 1A or 1B, or at those recommended by the manufacturer — since the rectifiers don’t float the batteries, float Voltage is not as critical), and alarm the battery charger currents per Part 4 of this table or the manufacturer’s recommendations.

Table 9 Alarm Thresholds on Analog Points
Part 1D:  DC Voltage Set Points for Lithium-based Batteries

| AID or SUB-AID | CONDTYPE | MJ, MN or CR | NOTES | THRESHOLDS |
| --- | --- | --- | --- | --- |
|  |  |  |  | LOWER | UPPER |
| N48B1 | LOW_VOLTAGE or HIGH_VOLTAGE | MINOR | Li-ion nominal 52 V float battery | -51.2 | -52.4 |
|  |  | MAJOR |  | -50.0 | -52.5 |
|  |  | MINOR | Lithium nominal 54.6 V float battery | -54.4 | -54.8 |
|  |  | MAJOR |  | -53.8 | -56.4 |

Table 13-5 Alarm Thresholds on Analog Points 
Part 1E:  DC Voltage Set Points for Converter Plants and Engine Start Batteries

| AID or SUB-AID | CONDTYPE | ALARM | NOTES | THRESHOLDS |
| --- | --- | --- | --- | --- |
|  |  |  |  | LOWER | UPPER |
| (none) or BATENGm or BATCHG | LOW_VOLTAGE or HIGH_VOLTAGE or VOLTAGE_OUT_OF _LIMIT | MAJOR | Plant output of a converter plant without batteries on the output bus should be set as near as possible to the nominal plant Voltage (e.g., 130 V) Float of engine start batteries should be per manufacturer recommendation | (2 V from the plant output Voltage setting |
|  | HIGH_VOLTAGE_HVSD | CRIT. | + or – 24 V plants + or – 48 V plants + or – 130 V plants |  | 28 V 56 V 137 V |

To prevent thermal runaway in VRLA batteries, the charge current flowing to the batteries can be limited by automatically lowering the float Voltage as the battery temperature rises (this is temperature compensation).  The recommended settings for temperature compensation devices are shown below (not all devices have each of these settings, so try to match those that apply to the particular device).  An attempt should be made to get as close as possible to these settings, but not all devices will be able to match these settings.  Voltage should not be lowered below open circuit to avoid severe loss of battery life.

Table 13-5 Alarm Thresholds on Analog Points Part 2:  Temperature Compensation and Current Limiting

| Optimum float Voltage at 77° F | -54.4 V (-52.2 for 23-cell string) |
| --- | --- |
| Lowest Voltage where compensation should stop | -52.0 V (-49.9 for 23-cell string) |
| Highest Voltage where compensation should stop | -56.0 V |
| Temperature at which compensation to lower the float should start | 77° - 86° F (25° - 30°C) allowable to automatically raise float from 40° - 30° F (5° to -1°C) |
| Maximum temperature at which compensation should end (to avoid taking the batteries below open-circuit Voltage — also reference the end Voltage above), or maximum Step Compensation Temperature | 135°F (57°C) |
| Final Step Temperature (temperature at which Voltage should be stepped 1-2 V below open circuit [-50 V]) | 160°F (71°C) |
| Maximum Battery Disconnect Temperature | 175°F (80°C) |
| slope of compensation | -1.3 to 3.0 mV/cell/°C rise |

Not all compensation is slope compensation.  An attempt should still be made to match the parameters shown above (except for the slope parameter) when step compensation is used.

Many existing rectifiers used with VRLA batteries in OSP locations have Voltage sensing circuits inaccessible by temperature compensation devices.  For these, to limit battery charge current, a Current Limiting device placed in series with each battery string may be used.  In addition, some devices perform both compensation and current limiting functions, offering even greater protection from thermal runaway.  The acceptable limits for current limiting devices are shown below:

Acceptable Limits:	Between C/8 and C/30

C is the Amp-hour rating of the string at the 8-hour rate to 1.75 V/cell.  For example, the current limit of a 100 A-hr battery string limited to C/20 would be 5 Amps.

Care must be taken to ensure that current limiting does not cause the plant to perform a High Voltage Shut Down while attempting to recharge the batteries.  This can happen on certain rectifiers if the current limiting is set too tightly.  For example, one type of rectifier may perform an HVSD while attempting to recharge if the current limiting is set for C/20.  In this case, the limits should be set for C/10.  Check the documentation of the suppliers of the current limiting device and power plant to see if this may be a problem.  Also, because discharge current as well as recharge current must pass through the current limiting device, ensure that the discharge current capacity of the device and its associated cabling is sufficient to meet the portion of the projected site load that will be placed on the individual string or group of strings served by the current limiting device.

There is no need to remotely report an alarm when temperature compensation or current limiting is active.  However, battery temperature alarms or battery current alarms may be set in accordance with the guidelines given in the other Parts of this Table 13-5.

Table 13-5 Alarm Thresholds on Analog Points                                           Part 3:  Temperatures

| SUB-AID | CONDTYPE | MJ, MN | DESCRIPTION | THRESHOLDS |
| --- | --- | --- | --- | --- |
|  |  | or CR |  | LOWER | UPPER |
| ROOM | LOW_TEMPERATURE or HIGH_TEMPERATURE or TEMPERATURE | MINOR | Room temperature is outside of "normal" operating temperature for the eqpt. CEV, hut, or other OSP controlled enviro. Controlled Environment Engine Room | 65˚ F 52˚ F 47° F | 81˚ F 95˚ F 93° F |
|  |  | MAJOR | When the room temperature reaches these, battery life or capacity is affected CEV, hut, or other OSP controlled enviro. Uncontrolled Engine Room Engine Room during Engine Run | 60˚ F 50˚ F 37° F 32°F | 85˚ F 100˚ F 128° F 128° F |
| BATm or BATmUP or BATmLO or BATmPC or Coolant | HIGH_TEMPERATURE or LOW_TEMPERATURE | MINOR | Flooded batt. temps. (especially on an upper tier) on charging can be several degrees higher than room temperature For VRLA batteries in a controlled environment. For VRLA batteries in a uncontrolled environment For Engine block/coolant/oil while idle | 64˚ F 52˚ F 27˚ F 87° F | 86˚ F 98˚ F N/A 123° F |
|  |  | MAJOR | For Flooded batteries For VRLA batteries in a controlled environment For Engine Coolant while running | 59˚ F 50˚ F N/A | 90˚ F 105˚ F 203° F |
| BATm | DIFFERENTIAL_TEMP | MINOR | Flooded batteries VRLA batteries |  | 8˚ F 13˚ F |
|  |  | MAJOR | Flooded batteries VRLA batteries |  | 12˚ F 20˚ F |

When room temperatures are alarmed, temperature measurements of flooded batteries are often unnecessary because their thermal mass keeps them relatively free of thermal runaway and in-line with room temperatures that are not widely varying.  The exception to this rule may be lead-antimony batteries.  When lead-antinomies begin to approach end-of-life, they are susceptible to thermal runaway, and monitoring of battery temperatures to detect this condition is desirable.

Because of the high susceptibility to thermal runaway of VRLA batteries, whenever a monitor is available at the site capable of monitoring battery and/or differential temperatures, this should be done; and is much more useful than room temperature, especially a differential temperature alarm in uncontrolled environments.

Table 13-5 Alarm Thresholds on Analog Points                                                    Part 4:  DC Current

| SUB-AID | CONDTYPE | MJ, MN | DESCRIPTION | THRESHOLDS |
| --- | --- | --- | --- | --- |
|  |  | or CR |  | LOWER | UPPER |
| BATm | CAPACITY_ EXCEEDED | MINOR (80%) MAJOR (100%) | Batteries should be engineered for a minimum of 4 or 8 hour reserve depending on whether there is an on-site engine. By alarming when battery discharge reaches this minimum; we’re alerted to add more strings due to growth. For example, a site with an engine, using 1680 A-hr. batts, is originally engineered for 6 hours to allow for growth — this is a discharge current in each string of approximately -240 A. As the load grows, the 4-hr. min. reserve is reached when each 1680 A-hr. string discharges approx. -295 A (the 4-hr. min. level for 4000 A-hr. cells is approx. -650 A; and the 8-hr. min. rate for 1680 A-hr. cells is approx. -190 A). By alarming at this level (or lower), there is warning to provide more batteries. | 80 to 100% of 4 or 8 hour discharge rating of battery |  |
|  | RECHARGE | MINOR or "Record Only" | This threshold is simply a status alarm to let the monitoring tech(s) know when the battery is recharging. Recharge will slow, the recharge current should drop below this threshold, and the alarm will go away. Set this at 2-6% of the 4 or 8-hr. discharge rate of the string. For example, the 4-hr. discharge rating of a 1680 A-hr. string is approximately 295 A. The alarm threshold could be set at 10 A. |  | (C/150 (wet cells) (C/50 (VRLAs) |
| Battery or Converter “plant" | CAPACITY_ | MINOR | The Plant or Converter being monitored is at 80-90% of its rated capacity. (Capacity equals bus bar or shunt capacity; or total rectifier/converter capacity of n-1; or 80% of total rectifier capacity — extra 20% allows for recharge.) |  | 80-90% of capacity |
|  | EXCEEDED | MAJOR | The Plant or Converter being monitored is at 100% of its rated capacity — which is bus bar or shunt capacity; or n-1 rectifier/converter capacity. |  | 100% or n-1 |
| CNTRL or DISTm | CAPACITY_ | MINOR | The Breaker or Fuse is nearing its engineered capacity |  | 80% |
|  | EXCEEDED or | MINOR | The Fuse or Breaker is near the engineered feeder capacity of the BDFB or feed to a Collocator |  | 40-50% |
| RECTm | OVER | MINOR | The Rectifier exceeds its rated capacity (for rectifiers that won’t current limit until a level above 120% due to their design, set it higher) |  | 111% |
|  | CURRENT | MAJOR |  |  | 120% |
| BATm | IMBALANCE | MINOR | This applies during both discharge and recharge if the current from this string exceeds the average current per string by this percentage. The average current per string is the total current flowing into or out of all strings divided by the number of strings (weighted relative to Amp-hr size if the strings are of different sizes). | 10% (wet) 30% (VRLA) | 10% (wet) 30% (VRLA) |
|  |  | MAJOR |  | 25% (wet) 50% (VRLA) | 25% (wet) 50% (VRLA) |

All possible current monitoring points may or may not be monitored depending on the situation.  This Tech Pub states that "major" power sources and Primary distribution source ends will be monitored.  The following table should be used to provide alarms as required.

AC Voltage measurements are defined as the rms (effective) Voltage difference between any two conductors of the circuit.  The actual level of the Voltage is determined by the phase of the circuit (single or 3 phase), configuration, and the base Voltage.

From Article 220.2 of the National Electric Code (NEC), the following Voltage levels should be used in AC computations:

- 120 V, 1-Ø

- 120/240 V, 1-Ø

- 208/120 V, 3-Ø, Y, where 208 can be used as a 1-Ø or 3-Ø Voltage, and 120 is 1-Ø

- 240 V, 3-Ø, , for 1-Ø or 3-Ø loads (a leg can also be center-tapped for 120V, 1-Ø)

- 480/277 V, 3-Ø, Y, where 480 is three-phase, and 277 is a single-phase Voltage

Because of this wide variation in Voltages, it is essential to ensure that the served equipment is properly configured for the provided Voltage, and the PSMC is configured to reflect the actual Voltage at a site.

Table 13-5 Alarm Thresholds on Analog Points                                                    Part 5:  AC Voltage

| SUB-AID | CONDTYPE | ALARM | DESCRIPTION | THRESHOLDS |
| --- | --- | --- | --- | --- |
|  |  |  |  | LOWER | UPPER |
| VOLTm or PHASEm | LOW_VOLTAGE or HIGH_VOLTAGE | MINOR | The AC Voltage being provided to the system is outside of acceptable levels. If the Voltage doesn’t return to normal, a tech must investigate | 95% | 105% |
|  | Or VOLTAGE_OUT_OF _LIMIT | MAJOR | The AC Voltage being provided to the system is dangerously outside of acceptable levels. Immediate action must be taken by a qualified power technician | 90% | 110% |

Table 13-5 Alarm Thresholds on Analog Points                                                    Part 6:  AC Current

| SUB-AID | CONDTYPE | ALARM | DESCRIPTION | THRESHOLDS |
| --- | --- | --- | --- | --- |
|  |  |  |  | LOWER | UPPER |
| CURNTm or PHASEm | CAPACITY _EXCEEDED | MINOR | The AC current exceeds engineered capacity of the protector. Set at 80% of capacity and/or Ampacity of feeder(s) or breaker/fuse |  | 80% |
|  | IMBALANCE | MINOR | One leg of the AC current to the system is out of balance with the other legs (based on the normal load current — which may have to be adjusted as the load grows). The situation should be investigated for possible engineering or installation errors, or phase failures | 85% | 115% |

Fuel Tanks come in all different sizes.  To have a common measuring point for sizing fuel tanks, they are sized based on engine run hours at full rated load.  The engine manufacturers will give gallons/hour consumption at this load, from which the tank size is computed; or similarly, the hours reserve remaining in the tank can be computed by dividing the consumption rate into the gallons.

Table 13-5 Alarm Thresholds on Analog Points                                                    Part 7:  Fuel Alarm Thresholds

| SUB-AID | CONDTYPE | MJ, MN | DESCRIPTION | THRESHOLDS |
| --- | --- | --- | --- | --- |
|  |  | or CR |  | LOWER | UPPER |
| MAINFUEL or DAYFUEL | LOW | MAJOR | The level in the fuel tank is at such a level that if a fuel order is not placed within the hour, and the engine is running, we may not get fuel to the site for a prolonged run. The minimum and the fuel tank size may be extended for very remote locations. | 25-33% (min. 12 hrs. @ full load or 20 hrs @ real load) |  |
|  | HIGH | MINOR | The tank has been overfilled |  | 90-95% |

## 13.6	Typical Power Alarm and Monitor Points

Because of limited numbers of points on PSMCs, it is not feasible to alarm everything in a site.  This section serves as a guide to which alarm, monitor, and control points to connect for different types of sites.

### 13.6.1	Typical PSMC-CL Points in Smaller Sites

The more information that can be communicated from a site with its “alarming” system, the better the analysis and dispatch will be.  A PSMC for Confined Locations (PSMC-CL) can convey the most information about a small site.  Sample PSMC-CL points are listed below in Parts 1A and 1B of Table 13-6.  Each of the analog points listed (e.g., plant Voltage, string current, etc.) will also have thresholds (listed in Table 13-5).

Table 13-6 Typical Power Alarm and Monitor Points                                                    Part 1A:  Typical Power Points for OSP Cabinets and Customer Premise (PSMC-CL)

| AID and sub-AID | CONDTYPE or ACTION | CR, MJ, or MN | TYPE | NOTES |
| --- | --- | --- | --- | --- |
| COMAC1 | COML_AC_FAIL | MJ | binary |  |
| N48B1 | MAJOR | MJ | binary | power plant major |
| N48B1 | MINOR | MN | binary | power plant minor |
| N48B1 | CRITICAL | CR | binary | power plant critical alarm |
| N48B1RECTm | FAIL | MN | binary | generic plant rect. fail (individuals if possible) |
| N48B1BATm | DIFFERENTIAL_TEMP | CR | binary | one per string if possible (battery - ambient) |
| N48B1DIST | FUSE/BRKR_OPERATE | MJ | binary | generic distribution fuse or breaker alarm |
| N48B1 | LOW_VOLTAGE | MJ | binary | plant low Voltage or battery on discharge |
| N48B1 | VERY_LOW_VOLTAGE | CR | binary |  |
| N48B1 | HIGH_VOLTAGE | MJ | binary |  |
| N48B1BATm | DISCONNECT | MJ | binary | individual strings or all batteries disconnected |
| RNG1 | MAJOR | MJ | binary | ring plant major (if there is a ring plant) |
| RNG1 | MINOR | MN | binary | ring plant minor |
| N48B1 | VOLTAGE |  | analog | plant Voltage |
| N48B1 | CURRENT |  | analog | plant current |
| ROOM | TEMPERATURE |  | analog | cabinet or room ambient temperature |
| N48B1BATmPC | TEMPERATURE |  | analog | one battery temperature per string (2 if possible) |
| N48B1BATmH1 | VOLTAGE |  | analog | first half Voltage per string |
| N48B1BATmH2 | VOLTAGE |  | analog | second half Voltage per string |
| N48B1BATm | CURRENT |  | analog | string current per string |

If there is a PSMC-CL that is not reporting via X.25/TL1, choose the most important points at the top of this list, and have them connected to the output contacts of the monitor.  Then connect these output contacts to the alarm device of the site.

Table 13-6 Typical Power Alarm and Monitor Points                                                    Part 1B:  Typical Power Points for CEVs, huts, CdOs (small COs without engines), and Radio Sites (PSMC-CL or PSMC)

| AID and sub-AID | CONDTYPE or ACTION | CR, MJ, or MN | TYPE | NOTES |
| --- | --- | --- | --- | --- |
| COMAC1 | COML_AC_FAIL | MJ | binary |  |
| N48B1 | MAJOR | MJ | binary | power plant major |
| N48B1 | MINOR | MN | binary | power plant minor |
| N48B1 | CRITICAL | CR | binary | power plant critical alarm |
| N48B1RECTm | FAIL | MN | binary | generic plant rect. fail (individuals if possible) |
| N48B1BATm | DIFFERENTIAL_TEMP | CR | binary | one per string if possible (battery - ambient) |
| N48B1DIST | FUSE/BRKR_OPERATE | MJ | binary | generic distribution fuse or breaker alarm |
| N48B1 | LOW_VOLTAGE | MJ | binary | plant low Voltage or battery on discharge |
| N48B1 | VERY_LOW_VOLTAGE | CR | binary | for ECS plants, these alarms are not distinct, & |
| N48B1 | HIGH_VOLTAGE | MJ | binary | the condition is "VOLTAGE_OUT_OF_LIMIT" |
| N48B1BATm | DISCONNECT | MJ | binary | individual strings or all batteries disconnected |
| RNG1 | MAJOR | MJ | binary | ring plant major (if there is a ring plant) |
| RNG1 | MINOR | MN | binary | ring plant minor |
| xC1 | MINOR | MN | binary | converter plant minor (converter fail) |
| xC1 | MAJOR | MJ | binary | converter plant major (other converter alm) |
| 1PHINV1 | FAIL | MJ | binary | inverter plant fail (if there is an inverter |
| N48B1 | VOLTAGE |  | analog | plant Voltage |
| N48B1 | CURRENT |  | analog | plant current |
| ROOM | TEMPERATURE |  | analog | cabinet or room ambient temperature |
| N48B1BATmPC | TEMPERATURE |  | analog | one batt. temperature per string (2 if possible) |
| N48B1BATmM | VOLTAGE |  | analog | midpoint Voltage per string |
| N48B1BATmPC | VOLTAGE |  | analog | pilot cell Voltage; one per string |
| N48B1BATm | CURRENT |  | analog | string current per string |
| COMAC1VOLTm | VOLTAGE |  | analog | AC Voltage per phase |
| COMAC1CURNTm | CURRENT |  | analog | AC current per phase |

A CEV, hut, Radio site, or small CO (CdO) may have one small battery plant, no engine, a ring plant, and may or may not have converters/inverters.  Therefore, there will not be many alarms.  Some of these sites will have a power plant controller that can be easily converted into a small PSMC (capable of analog and control features) with the simple addition of a circuit pack.  Again, this list is prioritized, so that those sites without a monitor may use the alarms at the top of the list first.

Radio sites generally have Negative 24 Volt plants instead of Negative 48 Volt plants.  Therefore, replace all N48 in the table above with N24.  The "x" above in the AID for converter plants means to replace it with the polarity and Voltage of the converter plant (e.g., N130).

### 13.6.2	Typical Central Office Power Alarm Points

The following Table lists “typical” central office power alarm points.  Central Office configurations and alarming vary so greatly, that it would be impractical to try to list every possible alarm found in these locations.  Therefore, this Table serves as only a guide to the most common points.  The table assumes the use of a PSMC in the site.

The numbers of points that can be monitored in mid-sized and larger COs are limited only to the number of points available on the PSMC.  The following table is a list of possible points that (it is not all-inclusive, but only suggestive of possible points) organized by priority under each heading.  The criticality (critical, major, or minor) of the alarm has not been included here.  It can be found in Table 13-2.  Each of the analog points (e.g., plant Voltage, etc.) will also have binary alarm set points (listed in Table 13-5).

Per Chapter 8 of this Tech Pub, several alarm points listed below are optional, dependent on whether there are enough available alarm points on the PSMC.  Use the information in Chapter 8 in conjunction with the available points on the site’s PSMC to determine which alarm points are to be used.

This site assumes one -48 V battery plant, one -130 V converter plant, and a single-phase 120 V inverter and UPS.  Sites with plants having other polarities and Voltages should substitute the appropriate AID, as per Table 13-1.  There may be more than one plant of a particular type.  Each plant will have its own points.

Table 13-6 Typical Power Alarm and Monitor Points Part 2:  Power Points for COs with Engines (page 1 of 2)

| AID and sub-AID | CONDITION TYPE | TYPE | NOTES |
| --- | --- | --- | --- |
| BATTERY/RECTIFIER PLANT |
| N48B1RECTm | FAIL | binary | generic plant rectifier fail (individuals if possible) |
| PSMCn or N48B1 | MAJOR | binary | backup generic major and minor from PSMC or |
| PSMCn or N48B1 | MINOR | binary | plant, connected to Dantel or other alarm device |
| N48B1DIST | FUSE/BRKR_OPERATE | binary | generic distribution fuse or breaker alarm(s) |
| N48B1 | LOW_VOLTAGE | binary | or taken as threshold off analog plant Voltage |
| N48B1 | VERY_LOW_VOLTAGE | binary | (optional) |
| N48B1 | HIGH_VOLTAGE | binary | or taken as threshold off analog plant Voltage |
| N48B1 | VOLTAGE | analog | plant Voltage |
| N48B1 | CURRENT | analog | plant current |
| N48B1ROOM | TEMPERATURE | analog | battery plant room ambient temperature |
| N48B1BATmPC | TEMPERATURE | analog | one battery temperature per plant |
| N48B1BATmM | VOLTAGE | analog | midpoint Voltage per string (optional) |
| N48B1BATmPC | VOLTAGE | analog | pilot cell Voltage; one per plant |
| N48B1BATm | CURRENT | analog | string current per string |
| N48B1RECTm | CURRENT | analog | individual rectifier currents (optional) |
| N48B1DISTm | CURRENT | analog | currents to larger individual loads (optional) |
| PSMCn | WATCHDOG | binary | PSMC failure run to Dantel or other alarm device |
| RING PLANT |
| RNG1 | MAJOR | binary | use only if other alarms that make up this major |
| RNG1 | MINOR | binary | and minor are not remoted to NMA |
| RNG1RGENm | FAIL | binary | generic or individual generator fail |
| RNG1INTERm | FAIL | binary | generic or individual interrupter fail |
| RNG1FUSE | FUSE/BRKR_OPERATE | binary | ring plant distribution fuse alarm |
| RNG1 | TRANSFER | binary | generator or interrupter transferred to backup |
| UPS |
| 1PHUPS1 | FAIL (or MAJOR) | binary | UPS fail or other major UPS alarm |
| 1PHUPS1 | MINOR | binary | any minor UPS alarm (non-service-affecting) |
| 1PHUPS1 | OFF_NORMAL | binary | UPS in an abnormal state (e.g., on bypass, etc.) |
| 1PHUPS1 | VOLTAGE | analog | UPS AC output Voltage (optional) |

Table 13-6 Typical Power Alarm and Monitor Points Part 2:  Power Points for COs with Engines (page 2 of 2)

| AID and sub-AID | CONDITION TYPE | TYPE | NOTES |
| --- | --- | --- | --- |
| INVERTER PLANT |
| 1PHINV1 | FAIL (or MAJOR) | binary | inverter plant fail or other inverter major alarm |
| 1PHINV1 | MINOR | binary | Inverter minor alarm (e.g., transferred, etc.) |
| 1PHINV1 | OFF_NORMAL | binary | inverter in manual bypass or other abnormal state |
| 1PHINV1 | VOLTAGE | analog | inverter output Voltage (optional) |
| 1PHINV1 | CURRENT | analog | inverter output current (optional) |
| COMMERCIAL AC |
| COMAC1 | COML_AC_FAIL | binary | to be monitored per phase, if possible |
| COMAC1TRNSW | RESTORE | binary | commercial AC restored (optional) |
| ACIN1PHASE | IMBALANCE | binary | (optional) |
| ACIN1VOLTm | VOLTAGE | analog | Voltage and current, measured on the load side of |
| ACIN1CURNTm | CURRENT | analog | the transfer switch (per phase in most cases) |
| STANDBY ENGINE |
| ENGALT1 | MAJOR | binary | use only if other alarms that make up this major |
| ENGALT1 | MINOR | binary | and minor are not remoted to NMA |
| ENGALT1 | STBY_ENG_FAIL | binary |  |
| ENGALT1TRNSWm | PROPER_OPERATION | binary | transfer switch operated (optional) |
| ENGALT1 | STBY_ENG_RUN | binary |  |
| ENGALT1BATCHG | FAIL | binary | engine start battery charger fail |
| ENGALT1 | CRANK_FAIL | binary |  |
| ENGALT1COOLANT | LOW_TEMPERATURE | binary |  |
| ENGALT1COOLANT | HIGH_TEMPERATURE | binary | (optional) if these alarms are combined into |
| ENGALT1 | OVERSPEED | binary | generic engine major and minor or engine fail |
| ENGALT1FAN | FAN | binary |  |
| ENGALT1OILPRESS | LOW | binary |  |
| ENGALT1MAINFUEL | FUEL_SYS_TRBL | binary | generic fuel system problem (e.g., leak, low fuel) |
| ENGALT1MAINFUEL | FUEL_LEAK | binary | (optional) if combined into generic fuel system |
| ENGALT1MAINFUEL | LOW | binary | trouble |
| ENGALT1BATCHG | VOLTAGE | analog | start battery Voltage |
| CONVERTER PLANT |
| N130C1 | MINOR | binary | use only if other alarms that make up this major |
| N130C1 | MAJOR | binary | and minor are not remoted to NMA |
| N130C1CONVm | FAIL | binary | generic or individual converter fail(s) |
| N130C1DIST | FUSE/BRKR_OPERATE | binary | generic converter distribution fuse alarm(s) |
| N130C1 | VOLTAGE | analog | plant Voltage |
| N130C1 | CURRENT | analog | plant current — if shunt available and accessible |

## 13.7	Power SNMP Traps for DSL and Ethernet Architectures

Most DSL and Ethernet based systems in Qwest report their alarms via SNMP Traps to MicroMuse’s NetCool™.  For Central Office based systems, the power plants that serve them report their alarms through NMA™.  However, in OSP locations (RTs and Prems), the power “housekeeping” alarms are either tied down to the DSL system housekeeping inputs as dry contacts and programmed in the DSL system to report SNMP traps, or (in the case of some UPSs) they have their own SNMP card to report traps over an IP link.

Table 13-7  SNMP Power Messages used in Qwest

| SEVERITY | SNMP Trap (Condition Description) |
| --- | --- |
| Major | acFailure |
| Major | batteryOndischarge |
| Minor | boostOn |
| Critical | communicationLost |
| Major | FuseFailure |
| Critical | lowBattery |
| Major | powerMajor |
| Minor | powerMinor |
| Minor | PowerShed |
| Major | upsBypass |
| Major | upsBypassacabnormal |
| Major | upsBypassacnormal |
| Major | upsBypassFreFail |
| Critical | upsDischarged |
| Critical | upsDiagnosticsFailed |
| Critical | upsOnBattery |
| Critical | upsOverload |
| Major | upsRebootStarted |
| Major | upsRecroterror |
| Major | upsScheduleShutdown |
| Major | upsSleeping |
| Major | upsTemp |
| Major | upsTest |
| Major | upsTurnedOff |

CONTENTS

Chapter and Section 	Page

14.	Power Audits	 14-1

14.1	Scope	 14-1

14.2	Power Plant Audit	 14-1

14.3	Check List	 14-1

14.3.1	Power Plants	 14-2

14.3.2	Batteries	 14-3

14.3.3	What Cable Racking is Required?	 14-3

14.3.4	How Much Cable is Piled on the Cable Rack and is any Blocked?	 14-3

14.3.5	Floor Loading of Equipment	 14-3

14.3.6	Converter Plants	 14-4

14.3.7	Ringing Plants	 14-4

14.3.8	AC Equipment	 14-4

14.3.9	Standby Engine Alternator	 14-4

14.3.10	Lighting	 14-5

14.3.11	Battery Distribution Fuse Boards (BDFBs)	 14-5

Tables

14-1	BDFB Capacity Table	14-6

# 14.	Introduction

## 14.1	Scope

This Chapter provides a procedure for auditing Power Plants in order to add or modify equipment.  Depending on the scope of the job requested by the Qwest Engineer, only portions of this may be necessary.

## 14.2	Power Audits

This Section provides a check list for performing an audit on power plants and their associated equipment.  When using this check list, an “overview” inventory of the site (using the forms in Chapter 15) may also be helpful.  Copies shall be made available for the Qwest Engineers and the local Power Maintenance Engineer.

## Check List

### 14.3.1.	Power Plants

  - What type of power plant and the Manufacturer?  (111A, 153, 154, 155, 302, 326, Lineage 2000 MCS, 1231H, 1231V, GPS, etc.)

14.3.1.1.1.	What is the model?

14.3.1.1.2.	If it is a WECO type plant is it a bus bar plant?

  - PBD location?

  - Power Plant Voltage, (-48, ±24, ±130V)?

  - What type of controller does the power plant have?

  - How many PBD bays?

  - How many cables (and their sizes) are there feeding each PBD bay?

    - Bay number 1

    - Bay number 2

    - Bay number 3

    - Bay number 4

  - List available fusing/circuit breaker locations, and sizes on plant.

    - Fuse/CB number, PBD number

    - Fuse/CB number, PBD number

    - Fuse/CB number, PBD number

    - Fuse/CB number, PBD number

  - Where is the plant main shunt located (if there is one)?

14.3.1.8.1.	Status of the main plant chandelier (if there is one)?

      - Where is the chandelier located?

        - What size is the chandelier bus bar (physical cross-sectional dimensions and laminations, or Ampacity)?

  - Are there enough connections available for rectifier(s), battery string(s), and PBD additions?

  - What is the drain on the power plant?

    - Plant meter reading.

    - PSMC reading (if applicable).

    - What is the reading of the main power plant shunt in millivolts?

    - What is the millivolt and Ampere rating of the main shunt?

  - How many rectifiers are in the plant now?

    - What type, model number, and current output?

    - What are the nameplate AC input Amps, Voltage, and phases (1 or 3) of the rectifiers?

    - Where are rectifiers fed from:  PDSC or main AC power board?

14.3.1.11.3.1	If it is from a PDSC what type, Ampacity rating and what size of circuit breaker feeds it?

    - Are the rectifiers operational, (do they turn on)?

    - Each rectifier ammeter reading.

      - Rectifier G1

      - Rectifier G2

      - Rectifier G3

      - Rectifier G4

      - Rectifier G5

      - Rectifier G6

      - Rectifier G7

      - Rectifier G8

      - Rectifier G9

      - Rectifier G10

  - Is there a PSMC monitoring system existing?  (Ratelco, DGU, etc.)

    - How many available points?

    - List of analog points?

    - List of binary points?

    - Have all alarms been tested and confirmed by the alarm center?

      - If yes what is the log number?

  - What type of equipment does the power plant feed?

    - IOF/Toll/Transport?

    - Isolated ground plane Switch?

    - Both?

    - If ESS is it 5E®, DMS®, or Ericsson?

  - Where is the ground window (if an ESS or shared plant)?

    - Is the ground window also the plant return bar?

    - Is the ground window a remote ground window?

    - Can the ground window be grown?

    - How many positions are available on the:

      - Integrated side?

      - Isolated side?

    - How many and what size of cables are powering the ground window MGB bar(s) if it is doubling as the plant return bar?

    - If the bar is feeding distribution, can the distribution be recabled to BDFB(s)?

  - Is the grounding adequate?  i.e.: 750 kcmil connected to plant discharge return bar and

    - No. 1/0 AWG main aisle framework ground.

  - Location of Power equipment

    - Is there physically enough room to add it?

    - Is it the best location?

    - Are there overhead obstructions?

    - What is the closest distance to equipment being fed?

    - Are there problems getting AC input to rectifier PDSCs?

- Batteries

  - How many battery strings are there in the plant now?

  - What type and size, (MCT II 4000, LCT1680, GU45, FTC21P, KS20472L1S etc.), and installation date for each string?

    - String A

    - String B

    - String C

    - String D

    - String E

    - String F

    - String G

    - String H

    - String J

  - Is each battery string equipped with shunts?

- What cable racking is required?

  - Ceiling height?

  - Is there any existing superstructure?

  - Will two levels of framing be required?

  - What types of connections are required to ceiling?  (Ceiling inserts, or imbedded Uni-Strut™?)

  - If there is no existing superstructure, can everything be supported from the floor?

  - Are there obstructions such as air vents/duct, pipes etc.?

    - No water pipe is directly above power equipment?

  - Is there proper sway bracing for E/Q zone if applicable?

- How much cable is piled on the cable rack and is any blocked?

  - Are cable holes full?

- Floor loading of equipment.

- Converter Plants

  - What is the location of the converter plant?

  - What is the model number of the converter plant?

  - Who is the manufacturer of the converter plant?

  - What is the Voltage of the converter plant?  (±24V, ±130V, etc.)

  - What is the load on the converter plant?

  - What is the feeding power plant?

    - What size is the fusing feeding the converters?

  - What are the quantities and sizes of the converters?

- Ringing Plants

  - What is the location of the ring plant?

  - What is the model number of the ring plant?

  - Who is the manufacturer of the ring plant?

  - What is the feeding power plant?

  - What is the ring generator model number?

    - How many ring generators are there?

  - What is the tone generator model number (if applicable)?

  - What is the interruptors’ model number (if applicable)?

- AC Equipment

  - What is the AC Voltage and phases available at the main HSP?

    - 208V, 240V, or 480V, and single or three-phase?

  - What are the Voltage and current readings at the HSP?

  - Can the HSP be added to safely?

  - Where does one go to get AC to power the rectifier(s)?

  - Are rectifiers powered from a step up or down transformer?

  - What is the circuit breaker or fuse size for the main AC entrance?

  - What is the cable size of the HSP conductors?

  - What is Ampere rating of the House Service Panel?

  - What is the transformer from the utility company rated at (kVA)?

- Standby Engine-Alternator

  - What was the load and date at the last engine run?

  - What is the kW rating of the standby set?

  - What is the size and type (above-ground, vaulted, etc.) of the main fuel tank?

  - What type of fuel does the standby set use (diesel, gas, propane)?

  - What is the engine start battery’s model and installation date?

  - What is the Battery charger size and type?

  - Is there a fuel tank monitor?

- Lighting

  - Is there DC task lighting available per Chapter 12?

  - Is there low level AC lighting in place in the power areas?

  - Is any lighting required for added equipment?

    - Where is power available for added lighting, and is it 120V or 277V?

- Battery Distribution Fuse Boards (BDFBs)

  - Is there physically enough room to add a BDFB?

  - Is the planned location for the BDFB the best location?

  - Are there overhead obstructions?

  - What is the closest distance to the equipment being fed?

  - Are there available fuse positions in the existing BDFB?

    - Are the fuse assignments records updated for the BDFB?

  - Complete Table 14-1 for each BDFB.  (Note:  There should be a minimum of 2 and a maximum of 8 feeder fuses for each BDFB)

    - If the LOAD is Greater than half the FUSE CAPACITY for any BDFB, that BDFB must be immediately embargoed for growth, a SAR must be generated by the Power Maintenance Engineer, and a direct call must be made to engineering to address the problem.

Table 14-1 BDFB Capacity Table

| BDFB LOCATION: |
| --- |
|  | Feeder Fuse Location | Fuse Capacity | Load Reading at BDFB or PBD |
| A FEEDER |  |  |  |
| B FEEDER |  |  |  |
| C FEEDER |  |  |  |
| D FEEDER |  |  |  |

CONTENTS

Chapter and Section 	Page

15.	Turn Up, Test and Acceptance Procedures	 15-1

15.1	General	 15-1

15.2	Maintenance Window Guidelines for Power	 15-1

15.3	Forms	15-3

Forms

820	Generic Test and Acceptance Checklist	15-4

821A	Power Room Lighting Test and Acceptance Checklist	15-5

821B	Alarm and/or Power Monitor/Controller (PSMC) Test and 
Acceptance Checklist	15-6

821C	BDFB, Power Board, or Fuse Panel Test and Acceptance Checklist	15-7

822	Batteries and Stands Test and Acceptance Checklist	15-8

823A	Rectifier Test and Acceptance Checklist	15-9

823B	Power/Battery Plant Test and Acceptance Checklist	15-10

824A	Converter Plant Test and Acceptance Checklist	15-11

824B	Residual Ring Plant Test and Acceptance Checklist	15-12

825A	Inverter Test and Acceptance Checklist	15-13

825B	UPS Test and Acceptance Checklist	15-14

826A	Standby Engine Test and Acceptance Checklist	15-15

826B	Transfer System and AC Service Entrance Test and Acceptance Checklist	15-16

826C	Fuel Tank, Fuel System, and Fuel Monitor Test and Acceptance Checklist	15-17

827	Outside Plant Site Test and Acceptance Checklist	15-18

828A	CO Grounding Test and Acceptance Checklist	15-19

828B	Power Distribution Bus Bar Test and Acceptance Checklist	15-20

829A	Power Area Floor Plan Test and Acceptance Checklist	15-21

829B	Power Documentation Test and Acceptance Checklist	15-22

840	Power Equipment Inventory	15-23

841	BDFB/PBD Panel Fuse/Breaker Assignment Record	15-24

844	Critical CO Power Alarm Verification	15-25

845	Outside Plant Power Equipment Inventory	15-26

846	Outside Plant Equipment Enclosure Housekeeping Alarm Verification	15-27

# 15.	Turn Up, Test and Acceptance Procedures

## 15.1	General

The attached forms are for use in all types of sites for performance of power turn up, test, and acceptance.  The forms are self-explanatory, with listings for notes, functions, and supporting documentation.  Supporting documentation for the functions will vary by site because there are many different manufacturers for each type of equipment.  Copies of most of these forms can also be found in Qwest Technical Publication 77350.  Three copies of each form shall be made; one shall be left on site with the job package, one shall be sent to the Qwest Engineer, and one shall be sent to the local Qwest Power Maintenance Engineer for that state.  Note that the forms do not start with Form number 1.  This is due to the fact that the forms originate from an internal Qwest power maintenance document, and in order to ensure that contracted installers and Qwest technicians are using the same form for the same activity, the form numbers of that document have been retained.

The installation provider is responsible for verifying that all the alarms are reporting correctly to the proper alarm center.  The installer must call the alarm center and ask them whether an alarm has been generated, and whether the names(s) of the alarm(s) generated correspond(s) to the alarm the installer initiated.  The installer shall then note the center response on the proper form(s).

## 15.2	Maintenance Window Guidelines for Power

A Maintenance (Installation) Window is a predetermined period during each day when specific planned maintenance and infrastructure provisioning work activities should be performed.  The purpose of scheduling work during specific times is to ensure a minimal amount of disruption to Qwest customers.  Although load and service conditions vary by site, nighttime is generally the time of least traffic in most Qwest sites.  Therefore the official Maintenance Window is:

Monday through Friday 10:00 p.m. to 6 a.m.

Saturday 10 p.m. to Monday 6 a.m.

For work that could affect DSL circuits, the Maintenance Window is midnight to 6 a.m. Sunday through Thursday

If in doubt, almost all Power work that involves even the slight possibility of taking down equipment should be done in the Maintenance Window to be safe, because nothing works without Power.  However, because local conditions for each site are more likely to be known locally, the final decision is left up to the local managers.

The following maintenance items should almost always be performed in the Maintenance Window:

- Battery Discharge tests of single string plants

- Building Power Blackout tests (annual engine run)

The following Power and Grounding Installation/Removal activities must be performed in the Maintenance Window.  These generally only apply to in-service or "hot" equipment, or the specific times when "dead" equipment is being connected to "live" equipment.  Power and Grounding Installation Guidelines are contained in Chapters 8, 9, and 10 of Qwest Technical Publication 77350.

- Any disconnections from the Ground Window MGB, CO Ground Bars, or main Horizontal or Vertical Equalizers while they are "in-service" should normally be Maintenance Window work

- Any connections or disconnections to the hot bus bars should almost always be done in the Maintenance Window (turning on a breaker or inserting  a fuse/fuse-holder does not require manual or tool touching of a hot bus, and therefore, may be done outside of the Maintenance Window; however, although connection of cables to "dead" fuse or breaker positions on the rear is not technically "hot", there are nearby hot busses, which may merit consideration for moving that work to the Maintenance Window)

- Any addition or removal of batteries from "live" strings (although it's desirable to do all this work in the Maintenance Window, it's only absolutely required for single string plants)

- Any connection or disconnection on the main AC power Board (feeder side) or any work on the AC transfer switch (see the exception above for the insertion of breakers) should be done in the Maintenance Window

Outside Plant locations (e.g., RT Cabinets, CEVs, huts, Customer Premises, etc.) deserve special Maintenance Window consideration due to access, lighting, and affected customers.  Note that, in all cases, the final decision is up to the local manager.  These managers also sign installation MOPs (even though Pub 77350 is geared towards CO work, the MOP process is recommended for OSP sites as well; especially Customer Premises sites, as per Pub 77368).  Some guidelines for OSP Power work, from NROC Power Tech Support, follow.  They apply to installation and maintenance activities described above, but modified by the following paragraphs.

- OSP sites/equipment with less than 96 DS0 (POTS) customers (equivalent to 4 or less T1s), might usually be exempted from the power Maintenance Window.  SHRPS/SHNS and other guaranteed services should usually follow the Maintenance Window, due to significant customer refunds for outages.

- For RT cabinets, night work may not be feasible in all cases (although small jobs may be done by flashlight or headlamp); due to the disruption that lighting, running trucks, generators, etc. can cause in neighborhoods.  In some neighborhoods, for some "planned" activities (especially routine maintenance), night work may cause more customer ill will than it prevents..

- For outdoor DSL cabinets, in cases where lighting, noise, etc. can be issues in the OSP as described above, the Maintenance Window may be extended to 8 a.m. with the permission of the local manager.

- Customer Premises installations are supposed to allow us 7 x 24 access, but this doesn't always happen.  For Customer Premises that allow 7 x 24 access, Maintenance Window guidelines should generally be followed due to the HiCap circuits/services usually located there.  Any Customer Maintenance Window should supersede our own (coordinate with them).

- Controlled environment electronic equipment enclosures (EEEs) include CEVs, CECs, huts, UEs, etc. generally have fiber, and/or enough POTS customers to warrant Maintenance Window guidelines being followed.

## 15.3	Forms

Qwest

###### GENERIC TEST & ACCEPTANCE CHECKLIST

| Site: | Job Number BVAPP: |
| --- | --- |
| Engineer: | Job Number Vendor: |
| Date of Installation completion: | Date of Vendor Departure: |
| Tested by: | Date: |
| ITEM | YES | NO |
| Equipment Verification |
| Frames located per floor plan |  |  |
| Installed per drawings |  |  |
| Equipment is what was ordered |  |  |
| Equipment options are correct |  |  |
| Spare equipment provided per ordering spec (if applicable) |  |  |
| Power feed to equipment checked |  |  |
| Workmanship |
| Frame alignment and equipment mounting |  |  |
| Relay rack numbering |  |  |
| Wiring and cabling |  |  |
| Equipment numbering and lettering |  |  |
| Cable openings sealed |  |  |
| Cable racks and other ironwork |  |  |
| Power and fusing (spare fuses available also) |  |  |
| Performance Tests |
| Tests per recommended equipment manual |  |  |
| Tests per Test & Acceptance package sent out with job (if applicable) |  |  |
| Documentation |
| "As-built" drawings sent back to engineering |  |  |
| Replacement drawings left on site |  |  |
| Initial battery charge reports (if applicable) |  |  |
| Equipment manuals received |  |  |
| Original test results retained |  |  |
| Alarms |
| Affected alarms tested prior to work start |  |  |
| Local and audible alarms (as applicable) tested prior to work start |  |  |
| Alarms installed and tested with Alarm Center (800-713-3666 or 800-258-8144) |  |  |
| Name of NROC Center Contact with whom alarms were tested: |
| Other |
| Comments (all No answers must be commented on) |

Form 820  Generic Test and Acceptance Checklist

Qwest

###### POWER ROOM LIGHTING TEST & ACCEPTANCE CHECKLIST

| Site: | Job Number BVAPP: |
| --- | --- |
| Engineer: | Job Number Vendor: |
| Date of Installation completion: | Date of Vendor Departure: |
| Tested by: | Date: |
| ITEM | YES | NO |
| 1. Lighting provided in the power areas is adequate, and located in accordance with the site record lighting plan drawing |  |  |
| 2. As a minimum, emergency/stumble lighting is available in stairwells; and task lighting over the control PBD, over the engine control panel and AC transfer system, over the main AC switchgear, and in the engine room |  |  |
| 3. Emergency egress/stumble and task lighting works |  |  |
| 4. Feeding fuse/breaker positions and emergency egress/stumble and task lighting fixtures are properly stenciled as to the equipment they feed or where they are fed from |  |  |
| Test & Acceptance should be performed with the installer on site. Note below all problems they fix: |
| Comments (all No answers must be commented on) |

Form 821A  Power Room Lighting Test and Acceptance Checklist

Qwest

ALARM AND/OR POWER MONITOR/CONTROLLER (PSMC)

TEST & ACCEPTANCE CHECKLIST

| Site: | Job Number BVAPP: |
| --- | --- |
| Associated Power Plant: | ANCR/PNAR #: |
| Engineer: | Job Number Vendor: |
| Date of Installation completion: | Date of Vendor Departure: |
| Tested by: | Date: |
| ITEM | YES | NO |
| 1. Complete copy of suppliers' manuals and drawings available on site |  |  |
| 2. Verify accuracy of the database, and ensure an electronic backup is made where applicable |  |  |
| 3. Verify that analog channel readings are within 1% of the values measured by plant meters or by technician's hand-held meter |  |  |
| 4. Bring in each binary alarm associated with this monitor (or other alarming device) and verify that technicians in Power NROC (800-713-3666) receive the alarm over NMA |  |  |
| A. There is local indication of the alarm on the monitor, if monitor is capable of this function |  |  |
| B. If monitor is capable and equipped, verify the difference between Minor Rectifier Fail (1 rectifier), and Major Rectifier Fail (2 or more rectifiers failed) |  |  |
| 5. Bring in binary alarms associated with the threshold settings of analog points (e.g., low Voltage, etc.), and ensure that these alarms report locally on the monitor and remotely to NMA |  |  |
| A. Analog points' binary thresholds are set properly (according to Chapter 13) |  |  |
| 6. If the monitor is controlling High Voltage Shutdown (HVSD), verify proper operation |  |  |
| 7. Ensure that all binary, analog, & control points requested on the job were provided, and ensure that there is a record left in the office on paper and/or on disk of the assignments |  |  |
| 8. Verify the difference between Minor Converter Fail (1 converter), and Major Converter Fail (2 or more converters failed) |  |  |
| 9. Verify security levels (e.g., different passwords), and dial-back numbers (if applicable) |  |  |
| 10. Verify that the system reboots properly after being turned off/on |  |  |
| 11. Verify through the NROC Center or NMA database group (800-258-8144) continuity of X.25 and/or IP link as applicable |  |  |
| 12. When monitor is equipped with control functions, verify proper operation of these functions (e.g., ring transfer, etc.) |  |  |
| 13. Verify that a laptop can communicate with the monitor over an RS-232 port |  |  |
| 14. Note the number of spare analog and/or binary points, and report them to Engineering |  |  |
| 15. Verify communication with the unit over a dial-up modem |  |  |
| Test & Acceptance should be performed with the installer on site. Note below all problems they fix |
| NOTE 1: Use supplier, Telcordia, and Qwest documentation as a guide to performing the tasks above. NOTE 2: When testing alarms and functions, be sure not to interrupt service unless absolutely necessary, and done during the Maintenance Window with notification to and signoff from appropriate personnel |
| Comments (all No answers must be commented on) |

Form 821B  Alarm and/or Power Monitor/Controller (PSMC) Test and Acceptance Checklist

Qwest

BDFB, POWER BOARD, OR FUSE PANEL

TEST & ACCEPTANCE CHECKLIST

| Site: | Job Number BVAPP: |
| --- | --- |
| Engineer: | Job Number Vendor: |
| Power Board &Fuse Numbers | BDFB Location |
| Date of Installation completion: | Date of Vendor Departure: |
| Tested by: | Date: |
| ITEM | YES | NO |
| 1. Proper equipment was ordered and is sized appropriately for the application |  |  |
| 2. Verify proper load bus arrangements by ensuring only 1 bus is hot with each feeder breaker on or fuse inserted |  |  |
| 3. Verify proper return bus options |  |  |
| 4. Verify accuracy & proper operation of the digital or analog meters & current shunts |  |  |
| 5. Test fuse alarms for proper operation and continuity to NROC (Note: PBDs generally monitored by the group at 800-713-3666, while BDFBs and other secondary fuse panels are monitored by the group at 800-258-8144) |  |  |
| 6. Verify proper placement, anchoring, and stenciling of the bay(s) and/or shelves |  |  |
| 7. Ensure that all fuse/breaker assignments are properly marked/stenciled for the loads they feed, and that all incoming and outgoing cables are properly tagged |  |  |
| 8. Verify proper connections of wires/cables to the fuse distribution, ground, and battery return busses/connections |  |  |
| 9. Verify proper cable routing |  |  |
| 10. Verify proper frame and central office grounding |  |  |
| 11. Report the number and type of spare fuse/breaker positions to Engineering |  |  |
| 12. Ensure that BDFBs are equipped with a sticker(s) specifying the maximum feeder load (50% of the protector size) for each feeder |  |  |
| Test & Acceptance should be performed with the installer on site. Note below all problems they fix |
| NOTE: Use supplier documentation as a guide to performing the tasks above. NOTE: Work on a Power Board or BDFB has the potential to interrupt service. Service shall not be interrupted when installing primary or secondary distribution panels. Cutover of a BDFB or Power Board should probably occur during the Maintenance Window if the power plant is already up and supporting loads. |
| Comments (all No answers must be commented on — use the back of this form if necessary) |

Form 821C  BDFB, Power Board, or Fuse Panel Test and Acceptance Checklist

Qwest

BATTERIES & BATTERY STANDS TEST & ACCEPTANCE CHECKLIST

| Site: | Job Number BVAPP: |
| --- | --- |
| Associated Power Plant: | Battery String #: |
| Engineer: | Job Number Vendor: |
| Date of Installation completion: | Date of Vendor Departure: |
| Tested by: | Date: |
| ITEM | YES | NO |
| 1. Battery stands and batteries are stenciled or identified with installation and/or manufacturing date (on batteries), string numbers/letters, and cell numbers (cell numbering is not required for 6/12 V monoblocs). |  |  |
| 2. Batteries and connectors are free of the following defects. |  |  |
| A. Cases crazed, cracked, bulged, corroded, or leaking |  |  |
| B. Level indicators missing or incorrect (for flooded batteries only) |  |  |
| C. Cover or post rise, and/or post corrosion |  |  |
| D. Excessive positive plate growth or strap growth for flooded cells with clear jars |  |  |
| E. Excessive plate bowing or cracking for flooded cells with clear jars |  |  |
| F. Excessive needle growth for flooded cells with clear jars |  |  |
| G. Lead-sulfate crystals for flooded cells with clear jars (check after initial charge) |  |  |
| 3. Electrolyte level is proper, and limits for electrolyte level are marked on batteries (for flooded batteries only). |  |  |
| 4. Proper vent and filler caps or funnels are installed, and flame arrestors are equipped with dust covers (for flooded batteries only). |  |  |
| 5. Battery records/logs and any manufacturer documentation is on-site and easily accessible. The Storage Battery report (RG47-0001) should have been filled out by the installation vendor. (This requirement is not applicable to 6/12 V monoblocks). |  |  |
| 6. Neutralizing agents and protective equipment are available nearby for use as required in the battery area: eyewash, absorbent pillows, neutralizer, rubber gloves, goggles, rubber apron. (This requirement is only applicable in buildings). |  |  |
| 7. Thermometers, hydrometers, and holders are furnished and mounted as required (for flooded batteries only). |  |  |
| 8. Check batteries and intercell connection integrity by placing string on a 5-minute discharge test into a real load or load box. (This requirement is optional if the string is installed into a new plant with no real load. At a minimum, attempt to determine if connections were properly tightened with a torque wrench.) |  |  |
| 9. All flooded battery cell Voltages are between -2.14 and -2.27 on float. |  |  |
| 10. Batteries and connections are properly marked and connected to +/-. |  |  |
| 11. Temperature compensation employed and working with VRLA batteries |  |  |
| 12. Spill containment (room/area or individual stand) installed for new flooded batteries in plants with at least 4 strings of 1680 AH or 2 strings of mini-tanks |  |  |
| 13. Battery Disconnects (when applicable) are sized per Chapter 3; and are wired to remote trip devices only when required. |  |  |
| 14. Battery stand is braced appropriately for earthquake zone in which site is located. |  |  |
| Test & Acceptance should be performed with the installer on site. Note on back all problems they fix. |
| Comments (all No answers must be commented on —additional room on back) |
| reference Routines EE200, EE201, EE202, EE757, EE758, EE759, EE660, and EE720 |

Form 822  Batteries and Stands Test and Acceptance Checklist

Qwest

RECTIFIER TEST & ACCEPTANCE CHECKLIST

| Site: | Job Number BVAPP: |
| --- | --- |
| Rectifier #’s: | Associated Power Plant: |
| Engineer: | Job Number Vendor: |
| Date of Installation completion: | Date of Vendor Departure: |
| Tested by: | Date: |
| ITEM | YES | NO |
| 1. Rectifiers are properly assembled, installed, and stenciled or identified. |  |  |
| 2. Correct type & capacity fuses are provided, & all fuses are clean & properly installed. |  |  |
| 3. AC power connections are properly made. Ensure proper transformer taps and phase rotation where applicable. |  |  |
| 4. Ensure that correct rectifier (size, type, AC input, etc.) was ordered, including correct wiring or apparatus options. |  |  |
| 5. Rectifiers operate per individual operation tests, and basic operational features work. |  |  |
| 6. Rectifier and/or Plant meters are accurate and properly adjusted. |  |  |
| 7. Alarm settings are adjusted to requirements, and proper alarm signals are transmitted (ensure alarms reach the NROC Center on 800-713-3666 or 800-258-8144). |  |  |
| 8. Current limiting and partial load features of units are set and adjusted properly. |  |  |
| 9. High Voltage shutdown (HVSD) feature operates properly, and all other DIP switches, potentiometers, and other options are properly set, including alarm thresholds. |  |  |
| 10. Outputs of all units are stable (non-hunting, except for load sharing variations), & rectifier float Voltages are properly set for battery type (see Chapter 13) & load sharing |  |  |
| 11. Simulate an AC power failure to verify that the units' auto-restart capability and current walk-in feature operate properly when AC power is restored. Ensure also that alarms clear and that the units return to float Voltage. |  |  |
| 12. All rectifiers are capable of operating, regulating, and current limiting at full load. |  |  |
| 13. Ensure AC fuse panel(s) feeding rectifiers have adequate spare capacity. |  |  |
| 14. For multi-phase fed rectifiers, verify appropriate operation or shutdown during phase failure if possible. |  |  |
| 15. Ensure proper selection and routing of rectifier control cables to plant controller. |  |  |
| 16. Ensure rectifier frames are properly grounded & that battery return cables are properly grounded & sized, dependent on whether plant is integrated, isolated, or combined. |  |  |
| 17. Ensure rectifier DC output cables are properly installed, & sized according to Chapter 2 (for 200 and 400 Amp rectifiers), or manufacturers’ recommendations (all other sizes). |  |  |
| 18. If the plant load exceeds the smallest rectifier size, ensure that each rectifier will carry full-rated load for at least 1 minute. |  |  |
| 19. Ensure that there is adequate ventilation & heat dissipation so rectifier will not overheat. |  |  |
| Test & Acceptance should be performed with the installer on site. Note below all problems corrected |
| NOTE: When testing alarms and functions, be sure not to interrupt service. Consider whether it is required to perform any of the tests in the Maintenance Window. |
| Comments on back of form (all No answers must be commented on) |

Form 823A  Rectifier Test and Acceptance Checklist

Qwest

POWER/BATTERY PLANT TEST & ACCEPTANCE CHECKLIST

| Site: | Job Number BVAPP: |
| --- | --- |
| Power Plant: | Location: |
| Engineer: | Job Number Vendor: |
| Date of Installation completion: | Date of Vendor Departure: |
| Tested by: | Date: |
| ITEM | YES | NO |
| 1. All battery distribution cables are of correct size and type, and properly terminated |  |  |
| 2. All equipment of control and distribution bays are correctly stenciled or identified |  |  |
| 3. All control circuit, charge, and discharge fuses and/or circuit breakers are of the correct type and capacity, and located as shown on the drawings |  |  |
| 4. Alarm fuse positions are equipped with correct fuses, and fuse and circuit breakers are properly designated as to the equipment they serve |  |  |
| 5. Verify alarms, locally, and to the Alarm Center (800-713-3666 or 800-258-8144) |  |  |
| 6. All DC meters are calibrated and properly adjusted |  |  |
| 7. All fuses are tight in their respective fuse holders, and fuses and circuit breakers are free of excessive heat |  |  |
| 8. The battery float Voltage is correct (check after meter calibration, and initial charging of the batteries) |  |  |
| 9. The Voltage alarm settings are correct per Chapter 13 |  |  |
| 10. Spare fuses are provided, and properly located & designated, near the battery plant |  |  |
| 11. If LVD is used (use only where required), ensure setting is -43.25 V or less, and that reconnect Voltage is no higher than -44 V.. |  |  |
| Test & Acceptance should be performed with the installer on site. Note below all problems they fix |
| Comments (all No answers must be commented on) |

Form 823B  Power/Battery Plant Test and Acceptance Checklist

Qwest

CONVERTER PLANT TEST & ACCEPTANCE CHECKLIST

| Site: | Job Number BVAPP: |
| --- | --- |
| Associated Power Plant: | Location: |
| Engineer: | Job Number Vendor: |
| Date of Installation completion: | Date of Vendor Departure: |
| Tested by: | Date: |
| ITEM | YES | NO |
| 1. The converter plant is properly assembled and installed (including properly made electrical connections), and stenciled or identified |  |  |
| 2. The input and output fuses are the correct type and capacity |  |  |
| 3. The discharge fuse alarms are operative and connected properly, and spare fuses are available |  |  |
| 4. The Voltage alarm levels are properly adjusted to specified limits |  |  |
| 5. All alarms function properly, and are received by the Alarm Center (800-713-3666 for COs and 800-258-8144 for Radio, IOF, and OSP sites) |  |  |
| 6. High Voltage shutdown (HVSD) feature operates properly |  |  |
| 7. The converter plant meters are accurate, and properly adjusted, and all other LEDs or other indicators work properly |  |  |
| 8. The output Voltage is adjusted within the specified limits, and can be accurately read from the test jacks |  |  |
| 9. The output current limit is properly set, as well as any other options set through DIP switches or potentiometers |  |  |
| 10. Verify that the converter plant functions properly under load (preferably up to the n-1 capacity, and preferably off-line on a load bank) for at least 30 minutes, and that there are no problems if the converters are switched on and off. |  |  |
| Test & Acceptance should be performed with the installer on site. Note below all problems they fix. |
| NOTE: When testing alarms and functions, be sure not to interrupt service unless done during off hours and with notification to appropriate personnel |
| Comments (all No answers must be commented on) |

Form 824A  Converter Plant Test and Acceptance Checklist

Qwest

RESIDUAL RING PLANT TEST & ACCEPTANCE CHECKLIST

| Site: | Job Number BVAPP: |
| --- | --- |
| Associated Power Plant: | Location: |
| Engineer: | Job Number Vendor: |
| Date of Installation completion: | Date of Vendor Departure: |
| Tested by: | Date: |
| ITEM | YES | NO |
| 1. The ringing plant is properly assembled, installed, and stenciled or identified |  |  |
| 2. Ringing plant fusing is in agreement with site drawings |  |  |
| 3. All alarms operate properly, including transfer alarms (ensure alarms reach Alarm center — 800-713-3666 for COs and 800-258-8144 for Radio, IOF, and OSP sites) |  |  |
| 4. The transfer feature operates automatically when a power failure occurs (for units when Ring Generator 1 is AC powered), or if Ring Generator 1 fails. (This transfer also applies to those sites equipped with interruptors besides the ring generators) |  |  |
| 5. If equipped, the transfer feature operates properly by manual or test transfer |  |  |
| 6. All Voltages, tone levels, and frequencies are within specified limits |  |  |
| 7. If meters are provided, they are accurate, and within adjustments |  |  |
| Test & Acceptance should be performed with the installer on site. Note below all problems they fix. |
| Comments (all No answers must be commented on) |

Form 824B  Residual Ring Plant Test and Acceptance Checklist

Qwest

INVERTER TEST & ACCEPTANCE CHECKLIST

| Site: | Job Number BVAPP: |
| --- | --- |
| Associated Power Plant: | Location: |
| Engineer: | Job Number Vendor: |
| Date of Installation completion: | Date of Vendor Departure: |
| Tested by: | Date: |
| ITEM | YES | NO |
| 1. The inverter plant is properly assembled and installed (including proper electrical connections), and stenciled or identified |  |  |
| 2. Input, output, and alarm fuses or breakers are the correct type and capacity, and output distribution is properly sized and connected |  |  |
| 3. Simulate an AC power failure. Ensure proper operation and transfer. During outage, check output Voltage and frequency. |  |  |
| 4. Verify that plant is capable of operation at full load; in either AC input or DC input modes. (Use a dummy load — e.g., load box — if necessary to fully load the plant) |  |  |
| 5. Verify proper operation of maintenance bypass, if equipped |  |  |
| 6. Alarms operate to the Alarm Center (800-713-3666) and clear properly |  |  |
| 7. Verify proper operation of any automatic shutdowns (e.g., low Voltage, emergency. stop, etc.) |  |  |
| 8. Verify proper operation of all controls and indicators (meters, LEDs, etc.) |  |  |
| 10. Ensure that a new ground reference is provided from a COGB, and that neutral and ACEG are tied together at the output |  |  |
| 11. Ensure there is adequate room and ventilation around the inverter plant |  |  |
| Test & Acceptance should be performed with the installer on site. Note below all problems they fix. |
| NOTE: When testing alarms and functions, be sure not to interrupt service unless done during off hours and with notification to appropriate personnel |
| Comments (all No answers must be commented on) |

Form 825A  Inverter Test and Acceptance Checklist

Qwest

UPS TEST & ACCEPTANCE CHECKLIST

| Site: | Job Number BVAPP: |
| --- | --- |
| Engineer: | Job Number Vendor: |
| Date of Installation completion: | Date of Vendor Departure: |
| Tested by: | Date: |
| ITEM | YES | NO |
| 1. The UPS is properly assembled, installed, and stenciled or identified in accordance with Engineering instructions |  |  |
| 2. The correct type and capacity fuses are provided, and all fuses are clean and properly installed |  |  |
| 3. AC/DC power connections are made in accordance with Engineering instructions, and in compliance with Qwest Technical Publication 77350, and this one |  |  |
| 4. Transformer taps are set properly |  |  |
| 5. Ensure proper AC phase rotation on the output |  |  |
| 6. Plant meters are accurate and properly adjusted |  |  |
| 7. Alarm settings are adjusted to requirements, and proper alarm signals are transmitted. Ensure that alarms reach the Alarm Center (800-713-3666). |  |  |
| 8. Correct wiring or apparatus options provided |  |  |
| 9. Current limiting and partial load features of units are set and adjusted per Engineering requirements |  |  |
| 10. High Voltage shutdown feature operates properly |  |  |
| 11. Outputs are stable (non-hunting, except for load sharing variations) |  |  |
| 12. Simulate AC power failure to verify unit's auto-switch capability, and that it operates properly when AC power is restored (ensure that alarms clear when AC is restored). Check for proper return to battery float Voltage |  |  |
| 13. UPS capable of operating at full load |  |  |
| 14. Battery chargers are operating at the required output Voltage |  |  |
| Test & Acceptance should be performed with the installer on site. Note below all problems they fix. |
| NOTE: Use supplier documentation as a guide to performing the tasks above. NOTE: When testing alarms and functions, be sure not to interrupt service unless done during off hours and with notification to appropriate personnel |
| Comments (all No answers must be commented on) |

Form 825B  UPS Test and Acceptance Checklist

Qwest

###### STANDBY ENGINE TEST & ACCEPTANCE CHECKLIST

| Site: | Job Number BVAPP: |
| --- | --- |
| Engineer: | Job Number Vendor: |
| Date of Installation completion: | Date of Vendor Departure: |
| Tested by: | Date: |
| ITEM | YES | NO |
| 1. Engine-alternators & associated equipment are located according to the floor plan drawings, & are installed according to Engineering request, & are properly sized (e.g., fuel and exhaust system piping & tubing) |  |  |
| 2. Engine start batteries and chargers are in good condition, and installed and operating properly |  |  |
| 3. Verify start batteries and charger per Forms 822, 823A, manufacturers’ documentation |  |  |
| 4. A remote emergency stop button is located outside but near engine room, & is properly identified & alarmed |  |  |
| 5. Test records, logs, and manufacturer documentation is on site and accessible |  |  |
| 6. Before operation, inspect for the obvious, like assembly; fuel or oil leaks; or loose, missing or damaged parts |  |  |
| 7. Fuel in main and day tanks is sufficient and free of excess water and other contaminants |  |  |
| 8. Oil and coolant levels are sufficient, fluids are contaminant-free, and jacket water heater is operational |  |  |
| 9. Engine-alternator operating instructions are posted near the engine, and are clear and easy to use |  |  |
| 10. Adequate ear and eye protection is available in the engine room, and adequate warning labels are posted |  |  |
| 11. Ensure that engine, engine room metallic parts & lines, and alternator neutral are all grounded per Pub 77355 |  |  |
| 12. Engine crankcase breather is vented to atmosphere or discharge damper |  |  |
| 13. With the engine manufacturer and the installer present perform a first test of the genset with the engine on at full-rated load (use a load bank) for 2-4 hrs (preferably run this test on site; however, the test may be done at the manufacturer’s location with Qwest present to observe). Observe all functions, readings, alarms, etc., & note abnormalities, paying special attention to the following: |  |  |
| A. Water, fuel, and oil temperatures and pressures are within limits |  |  |
| B. Ensure proper operation of the transfer switch |  |  |
| C. Frequency, current, kW, and Voltage readings are correct, and within limits |  |  |
| D. Test all alarms during run, both locally and to the Alarm Center (800-713-3666) for proper operation |  |  |
| E. If provided, rectifier sequencing functions properly |  |  |
| F. Exhaust pressure is less than limits; no exhaust leaks; internal exhaust pipes insulated; 9" minimum exhaust clear from combustibles; hot "reachable" parts guarded/insulated and/or labeled; exhaust couplings use bolted flanges with gaskets or threaded pipe; has a flexible connection to engine and flexible supports to allow for expansion/contraction; and end of exhaust stack protected |  |  |
| G. Ensure proper operation of all fuel pumps, and the day tank (where applicable) |  |  |
| H. Intake/exhaust fans/louvers operate (and held open by spring on power loss), and are properly sized per drawings. (Check proper intake size by seeing if engine room door opens easily). Air intake filters are properly installed. (Exhaust fans to be controlled by room thermostat, if separate.) Exhaust is positioned so that its gasses & heat are not part of the intake air. |  |  |
| I. If provided, paralleling functions properly |  |  |
| J. Current load is reasonably balanced between phases |  |  |
| K. All required gauges, meters, and local and remote alarms are present as per Chapters 8 and 13 |  |  |
| L. Test the emergency shutdown |  |  |
| 14. Check fluids and fuels after run, and visually inspect for leaks, loose parts, etc. |  |  |
| NOTE: Use supplier engine Test and Acceptance too; and when testing alarms and functions, don’t interrupt service |
| Comments (all No answers must be commented on — Please use the back of this form for comments) |

Form 826A  Standby Engine Test and Acceptance Checklist

Qwest

TRANSFER SYSTEM AND AC SERVICE ENTRANCE

TEST & ACCEPTANCE CHECKLIST

| Site: | Job Number BVAPP: |
| --- | --- |
| Engineer: | Job Number Vendor: |
| Date of Installation completion: | Date of Vendor Departure: |
| Tested by: | Date: |
| ITEM | YES | NO |
| 1. Ensure proper operation of the transfer system. Simulate an AC failure and return of Commercial AC. Ensure that all timers function properly. |  |  |
| 2. If provided, paralleling functions properly and that there are sequencer lights or meters, which properly operate if paralleling, is to be done manually. |  |  |
| 3. Ensure that drawings for the transfer system are on site. |  |  |
| 4. Ensure that a single line-drawing is on site (it may be physically etched or drawn on the AC switchgear) |  |  |
| 5. Visually inspect (or thermally with a thermal gun or camera) all connections in the transfer system and AC service entrance cabinets for tightness. |  |  |
| 6. Ensure that the AC loads of the site do not exceed bus bar and breaker capacities in the AC switchgear. |  |  |
| 7. Ensure that electrical safety equipment is available for the site: electrical gloves, goggles, tags/locks for use in lockout/tag out procedures when AC work is being done, & possibly fire-retardant Nomex gear. |  |  |
| 8. Ensure that AC service entrance has a lightning arrestor and/or surge suppressor properly installed. |  |  |
| 9. Ensure that the AC fail is monitored per phase, and that an AC fail alarm properly reports to the Alarm Center (800-713-3666) |  |  |
| 10. If the site is equipped with a power monitor (PSMC), verify that AC Voltage (per phase, line-neutral) and currents (per phase) are monitored and reading properly. |  |  |
| 11. Ensure that the power company transformer is adequately sized to handle the site load. |  |  |
| 12. Ensure that the AC Service Entrance and Transfer System are grounded per Pub 77355 |  |  |
| 13. Ensure that there is proper interrupt current rating coordination from the power company transformer down to the PDSCs (e.g., ensure that the k.A.I.C of the service entrance equals or exceeds that of the power company transformer, etc.) |  |  |
| NOTE: Use supplier documentation, for Test and Acceptance NOTE: When testing alarms and functions, be sure not to interrupt service |
| Comments (all No answers must be commented on — Please use the back of this form for additional comments) |

Form 826B  Transfer System and AC Service Entrance Test and Acceptance Checklist

Qwest

FUEL TANK, FUEL SYSTEM, AND FUEL MONITOR

TEST & ACCEPTANCE CHECKLIST

| Site: | Job Number BVAPP: |
| --- | --- |
| Engineer: | Job Number Vendor: |
| Date of Installation completion: | Date of Vendor Departure: |
| Tested by: | Date: |
| ITEM | YES | NO |
| 1. Fuel in main and day tanks is sufficient and free of excess water and other contaminants |  |  |
| 2. Ensure that outdoor tanks are placed so that water will not flow into them or pool on top of them. |  |  |
| 3. If the outdoor Diesel fuel tank is aboveground in a climate where temperatures may get below 32˚ F, ensure that the tank either is using winter blend Diesel fuel, or is equipped with a tank heater. |  |  |
| 4. Visually ensure that all fuel tanks (both main and day) have containment that will contain all of the fuel in the tank in case of a leak. |  |  |
| 5. Inspect tank(s) and all fuel piping and pumps for any leaks |  |  |
| 6. Ensure fuel lines are connected to engine through a flexible section |  |  |
| 7. Fuel Lines installed and routed in accordance with the vendor-supplied Engineering specs and drawings. |  |  |
| 8. Verify that an anti-siphon valve is installed on the fuel suction line at the first entrance point to the generator room or enclosure when the main tank is higher than the engine or day tank. (In some jurisdictions, the fuel line is required to have a meltable link valve that closes in case of fire.) |  |  |
| 9. Verify that an electric fuel solenoid (operating from the engine start and/or control batteries at 12 V or 24 VDC) is installed on the supply line. The solenoid must be connected to the generator run circuit in the control panel. This solenoid should close when the emergency stop button is pushed. |  |  |
| 10. Verify that fuel lines running on the floor are routed so as not to create a safety hazard. (Fuel lines lying on the floor should be covered with a metal shroud painted yellow or yellow with black diagonal stripes.) |  |  |
| 11. Verify that the fuel lines are Aero-quip or Stratoflex hose or black iron. (Aero-quip and Stratoflex lines are permitted, but must be run inside a containment conduit. Galvanized pipes and fittings are not permitted.) |  |  |
| 12. Verify that the fuel return line is free from all obstructions. (No gates, valves, or traps are permitted.) |  |  |
| 13. Ensure proper operation of all fuel pumps, plus any day tank valves |  |  |
| 14. Ensure that a low fuel alarm is reported (may be reported as a generic fuel system trouble) all the way to the Alarm Center (800-713-3666). The low fuel alarm should report when there is 8 hours or more of fuel. |  |  |
| 15. If the site is equipped with a fuel tank monitor, ensure that it has at least a generic fuel system trouble alarm wired and reporting all the way to the Alarm Center (800-713-3666). |  |  |
| 16. Ensure fuel tank monitor is equipped with a dialup modem and a working phone line (some radio sites and other sites where phone service is inaccessible may be exempt from this requirement), and that the Power Alarm Center and the local Power Crew have that number. |  |  |
| 17. Ensure that the fuel tank monitor is equipped with paper tape and ink, and a method of storing the tape. |  |  |
| 18. If the tank is vaulted, and the vault is an OSHA-defined “confined space”, ensure that it is so marked |  |  |
| 19. Ensure that all fuel lines and tanks are properly grounded in accordance with Qwest Tech Pub 77355. |  |  |
| NOTE: Use supplier documentation for Test and Acceptance; and when testing alarms and functions, don’t interrupt service |
| Comments (all No answers must be commented on — Please use the back of this form for comments) |

Form 826C  Fuel Tank, Fuel System, and Fuel Monitor Test and Acceptance Checklist

Qwest

OUTSIDE PLANT SITE TEST & ACCEPTANCE CHECKLIST

| Site: | Job Number BVAPP: |
| --- | --- |
| Engineer: | Job Number Vendor: |
| Date of Installation completion: | Date of Vendor Departure: |
| Tested by: | Date: |
| ITEM | YES | NO |
| 1. Ensure that internal and external grounding is per Qwest Technical Publication 77355. Ensure proper grounding of the site using an earth resistance tester (meg-ohmmeter). |  |  |
| 2. Do ventilation and exhaust openings have free access |  |  |
| 3. Ensure that the site and all of the bays and wiring in the RT are properly tagged/stenciled |  |  |
| 4. Ensure proper operation of A/C, sump pump, gas monitor and other environmental systems with the vendor present for CEVs, CECs, and huts, as applicable |  |  |
| 5. Ensure safety equipment (e.g., fire extinguisher, first aid kit, gloves, eyewash fluid, etc.) is present, as applicable |  |  |
| 6. Ensure that all holes in a CEV are properly sealed |  |  |
| 7. Emergency lighting, gas monitors, environmental controllers, or any other device that should be powered by -48 VDC is connected to the DC Plant. |  |  |
| 8. Site is properly constructed, landscaped, and backfilled; and weeds are abated |  |  |
| 9. Portable genset connection available and sized properly. Verify that a genset can be parked within 30 ft of the transfer system, and that the soil is such that there is access under adverse weather conditions. After turn-up, transfer the site to the engine to confirm backup. |  |  |
| 10. Site has records/forms for proactive maintenance of the power plant. Ensure that the power plant was turned up correctly per Forms 822 through 823B. Load test the plant & batteries. |  |  |
| 11. Ensure continuity of power and environmental alarms, and any other alarms to the Alarm Center at 800-258-8144. (Power Major, Power Minor, Intrusion, High Temperature, and Explosive Gas Alarm for CEV/Cs are a minimum.) If a mux is used for housekeeping alarm transport, verify that it is configured for phase 2 and provisioned for X.25/TL1. (See Chapter 13 for power and environmental alarm standards.) |  |  |
| 12. Lightning/surge arrestor installed in power pedestal, and power pedestal wired per NEC |  |  |
| 13. Confirm that controlled environment sites are set to operate within 55-85° F. |  |  |
| This checklist should be performed with the installer(s)/contractor(s) on site. Note below all problems they fix. |
| Comment below or on back (all No answers must be commented on) |

Form 827  Outside Plant Site Test and Acceptance Checklist

Qwest

CO GROUNDING TEST & ACCEPTANCE CHECKLIST

| Site: | Job Number BVAPP: |
| --- | --- |
| Engineer: | Job Number Vendor: |
| Date of Installation completion: | Date of Vendor Departure: |
| Tested by: | Date: |
| ITEM | YES | NO |
| 1. The site ground is the proper size, and installed in accordance with the site record drawings, Engineering instructions, and Qwest Technical Publication 77355 |  |  |
| 2. Both ends of all site ground cables are tagged, and designated to show opposite end terminating location |  |  |
| 3. If ground leads are run through metallic conduit both ends of the conduit or sleeve are bonded to the ground lead. |  |  |
| 4. Isolated frames, cabinets, rectifiers, etc. containing AC service are properly grounded per Tech Pub 77355 Chapters 8 and 9 |  |  |
| 5. If associated switching system uses isolated grounding, integrity must meet the system requirements spelled out in Qwest Technical Publication 77355 |  |  |
| Test & Acceptance should be performed with the installer on site. Note below all problems they fix |
| For a complete grounding review, contact the Qwest Power Maintenance Engineer |
| Comments (all No answers must be commented on) |

Form 828A  CO Grounding Test and Acceptance Checklist

Qwest

POWER DISTRIBUTION BUS BAR & CABLING

TEST & ACCEPTANCE CHECKLIST

| Site: | Job Number BVAPP: |
| --- | --- |
| Associated Power Plant: | Location: |
| Engineer: | Job Number Vendor: |
| Date of Installation completion: | Date of Vendor Departure: |
| Tested by: | Date: |
| ITEM | YES | NO |
| 1. AC bus duct and conduit is installed in accordance with site record drawing layout, and the manufacturers' specifications |  |  |
| 2. The proper type and size fuses and/or circuit breakers are installed in AC bus duct plug-in units |  |  |
| 3. Warning labels are placed at all access openings and end sections of AC bus duct, as required |  |  |
| 4. Bus bar is installed in accordance with site record drawing layout |  |  |
| 5. Bus bars and risers are stenciled to properly identify CHARGE, DISCHARGE, BAT, GRD, RTN, Voltage, etc. |  |  |
| 6. The ammeter shunt is properly mounted and stamped to indicate Voltage and Ampere rating |  |  |
| 7. Installation meets Qwest workmanship standards, and is in accordance with Engineering standards and drawings, as spelled out in Qwest Technical Publications 77350, 77351, 77352, 77355 and this one |  |  |
| 8. Bus bars, joints, and terminating connections to bus bars are free of excessive heat. (Technicians may use contact thermometers, or infrared temperature guns to determine heating. If major problems are suspected, a Qwest Power Maintenance Engineer or outside thermographer may be called in to do a thermal camera scan.) |  |  |
| 9. Power cable is routed in accordance with site record drawings |  |  |
| 10. Power cable is run and secured on cable racks |  |  |
| 11. Adequate insulating protection is provided on cable rack straps, stringers, thread rods, auxiliary frame bars, and other metallic objects where power cable makes contact with sharp surfaces |  |  |
| 12. Power cable insulation is free of damage |  |  |
| 13. Terminating wires and cables are properly tagged and designated at both ends of conductors when required |  |  |
| 14. All cables listed on power cable running list are installed with correct type and size of cable as specified, or otherwise calculated |  |  |
| Test & Acceptance should be performed with the installer on site. Note below all problems they fix. |
| Comments (all No answers must be commented on) |

Form 828B  Power Distribution Bus Bar and Cabling Test and Acceptance Checklist

Qwest

POWER AREA FLOOR PLAN TEST & ACCEPTANCE CHECKLIST

| Site: | Job Number BVAPP: |
| --- | --- |
| Associated Power Plant: | Location: |
| Engineer: | Job Number Vendor: |
| Date of Installation completion: | Date of Vendor Departure: |
| Tested by: | Date: |
| ITEM | YES | NO |
| 1. Power equipment is located and designated as shown on floor plan drawing |  |  |
| 2. All cable holes appear to be closed properly (wall, ceiling, and floor type, as applicable) |  |  |
| 3. Wall and column mounted equipment are properly located and shown on floor plan, cable rack plan, or other associated site record drawings |  |  |
| Test & Acceptance shall be performed with the installer on site. Note below all problems they fix. |
| Comments (all No answers must be commented on) |

Form 829A  Power Area Floor Plan Test and Acceptance Checklist

Qwest

POWER DOCUMENTATION TEST & ACCEPTANCE CHECKLIST

| Site: | Job Number BVAPP: |
| --- | --- |
| Associated Power Plant: | Location: |
| Engineer: | Job Number Vendor: |
| Date of Installation completion: | Date of Vendor Departure: |
| Tested by: | Date: |
| ITEM | YES | NO |
| 1. All new power equipment drawings furnished on this project are in acceptable condition |  |  |
| 2. All power drawings that were supposed to be provided with this job were provided |  |  |
| 3. All operating and maintenance instructions for new or added power equipment are available and accessible at the site |  |  |
| 4. All installer job completion reports are available |  |  |
| 5. Installer(s) followed written MOPs |  |  |
| Test & Acceptance should be performed with the installer on site. Note below all problems they fix. |
| Comments (all No answers must be commented on) |

Form 829B  Power Documentation Test and Acceptance Checklist

Qwest

CENTRAL OFFICE POWER EQUIPMENT INVENTORY

| OFFICE: |  | CLLI: |  | DATE: |  |
| --- | --- | --- | --- | --- | --- |
| ADDRESS: |  | TECH: |  | PHONE: |  |
| BATTERY PLANTS |
|  | Plant #1 | Plant #2 | Plant #3 |
| Voltage & Polarity: |  |  |  |
| Plant/Controller Mfg/Mdl |  |  |  |
| Plant Size (shunt/bus Amps) |  |  |  |
| Rectifier Qty & Models: |  |  |  |
| Battery Strings & A-hr Size: |  |  |  |
| Battery Mfgs & Models: |  |  |  |
| Battery Installation Dates: |  |  |  |
| Plant Load in Amps: |  |  |  |
| PDSC Bus/Feed Brkr Size: |  |  |  |
| Add Rect. max AC loads |  |  |  |
| CONVERTER PLANTS |
|  | Plant #1 | Plant #2 | Plant #3 |
| Voltage & Polarity: |  |  |  |
| Mfg& Model: |  |  |  |
| Associated Battery Plant: |  |  |  |
| Qty & Sizes of Converters: |  |  |  |
| Plant Load in Amps: |  |  |  |
| RING PLANT(S) | PSMC MONITOR and OTHER ALARM DEVICES |
| Mfg/Model: | RR: | PSMC Mfg & Model: |
| Ringers: | Interrupters: | Software Version: |
| Tone Generators: | Installation Date: | Dial-Up #: |
| INVERTER(S)/UPS | X.25/IP Ckt #: |
| Mfg & Model: | Other Alarm Devices (e.g., Dantel, etc.): |
| Size, AC Voltage/Phase: | ENGINE & TANK DATA |
| Load (AC Amp/kVA): | Engine Mfg& Model: |
| Associated Battery Plant: | Voltage & kW: |
| Installation Date: | Install Date (note if not Autostart): |
| COMMERCIAL AC | Fuel Type & Consumption (gal/hr): |
| Voltage & Phase: | Actual Engine Load (in kW): |
| Size (Amps): | Start Batt Mfg& Model: |
| Lightning Arrest Frame & Model: | Start Batt Install Date: |
| PORTABLE GENSET INFORMATION | Transfer System Type/Size: |
| Plug Frame, Mod, & Size (Amps): | Day Tank Capacity (gal): |
| Portable Frame, Size, Fuel: | Main Tank Type & Capacity (gal): |
| Storage Location: | Tank Monitor Mfg & Model: |
| NOTES & COMMENTS (use back of sheet as needed) | Tank Monitor Dialup: |
| Retain a copy of this form and send a copy to the Qwest Power Engineers |

Form 840  Central Office Power Equipment Inventory

Qwest

BDFB OR POWER BOARD PANEL FUSE/BREAKER ASSIGNMENT RECORD

| Site: | CLLI: | Date: |
| --- | --- | --- |
| Address: |
| Tech: | Phone/Pager: |
| PBD/RR of this BDFB/PBD: | PANEL(s): |
| Feeder Fuse/Breaker PBD & Position: | Feeder Fuse/Breaker Size: | Panel Load: |
| Position | Equipment & Relay Rack Fed | Fuse or Brkr Size | Mfg L-2 Drain | Mfg L-1 Drain | Actual Load |
| Totals |  |  |
| Additional panels may be placed on additional sheets. List 2 drains are peak drains sized at 125% minimum of this; and cable sized from them too List 1 drains are average drains Assigning fuses from the bottom to the top of a bay or panel (or inside to outside for horizontal panels) eases future installation and reduces cable congestion as needed Contact your Design Engineer for a fuse assignment (if those are tracked in your area) Please note if this Panel is "bussed" or "cabled" in the rear to adjacent panels (e.g., C, A2, etc.) Information for all columns may not be available to you — some columns are for Engineering use, and some for the "field" |
| Notes: |

Form 841  BDFB/PBD Panel Fuse/Breaker Assignment Record

Qwest

CRITICAL CO POWER ALARM VERIFICATION

| Alarm | NMA ticket # | Notes |
| --- | --- | --- |
| Critical Power Alarms |
| Commercial AC Fail |  |  |
| Power Major |  |  |
| Power Distribution Fuse/Breaker Major |  |  |
| Low Voltage and/or Battery on Discharge |  |  |
| Very Low Voltage (if applicable) |  |  |
| High Voltage |  |  |
| Rectifier Fail Major |  |  |
| Ring Plant Major |  |  |
| Low Voltage Disconnect (where applicable) |  |  |
| Engine Run |  |  |
| Engine Fail/Major |  |  |
| Low Fuel / Fuel System Trouble |  |  |
| Alarm Center Contact Person: | Alarm Center Phone: |
| Site CLLI: | Site Address: |
| Alarm Telemetry System Type: |
| X.25 or IP (PSMC) | e-tel (Dantel, E2A, etc.) | Switch or other |
| Installer performing the test and company | Phone: |
| NROC Tech with whom Test performed: | Phone: |
| It may not be wise to test some alarms except in the Maintenance Window due to the possibility to cause an outage if they are truly tested; and/or in some cases, it may be best to simply verify alarm continuity by shorting the alarm pins instead of actually bringing in the alarm, for the same reasons |
| Additional Notes: |

Form 844  Critical CO Power Alarm Verification

Qwest

OUTSIDE PLANT POWER EQUIPMENT INVENTORY

| Common Name of Location |  |
| --- | --- |
| State |  |
| CLLI |  |
| Address |  |
| Upstream Office (serving Wire Center) |  |
| Access & Directions |  |
| Map or GPS coordinates |  |
| Customer (primarily for Customer Prem sites) |  |
| Site Type (RT, CEV, UE, CEC, hut, rptr, CPE) (List RTs by type: e.g., 80 cabinet, etc.) |  |
| Date of this review |  |
| Reviewer name & contact # |  |
| Air-conditioning type & maintenance contact |  |
| Power plant type (also list J-spec, KS-, or mdl ) |  |
| Load (in Amps) |  |
| # Rectifiers |  |
| Rectifier type [also list the model number(s)] |  |
| Rectifier size(s) |  |
| Float Voltage |  |
| # Battery strings |  |
| Battery type (model #, KS-spec, etc.) |  |
| Battery size (A-hrs) |  |
| # cells/monoblocs per string |  |
| Battery installation date(s) |  |
| Residual Ring plant type (model number, etc.) |  |
| Comm. AC Voltage, phase, and Amp rating |  |
| Generator Plug Mfg., type, and size |  |
| Alarm system (E-tel, X.25, overhead, etc.) |  |
| Alarm Center & Center phone # |  |
| CIRCLE ALARMS THAT ARE PRESENT (Add any others not listed here) POWER MJ POWER MN RECT. FAIL AC PWR FAIL |
| Notes: |

Form 845  Outside Plant Power Equipment Inventory

Qwest

OSP EQUIPMENT ENCLOSURE POWER ALARM VERIFICATION

| Alarm | Works? | Doesn’t Work? | N/A |
| --- | --- | --- | --- |
| Commercial AC Fail |  |  |  |
| Power Major |  |  |  |
| Power Minor |  |  |  |
| High Battery Temperature |  |  |  |
| Power Distribution Fuse/Breaker |  |  |  |
| Low Voltage and/or Battery on Discharge |  |  |  |
| Very Low Voltage |  |  |  |
| High Voltage |  |  |  |
| Rectifier Fail (list the number of these alarms if more than 1) |  |  |  |
| Ring Plant Major |  |  |  |
| Ring Plant Minor |  |  |  |
| High Temperature (of the enclosure) |  |  |  |
| Explosive Gas Alarm |  |  |  |
| Toxic/Explosive Gas Alarm (combined) |  |  |  |
| Ventilation/Fan Fail |  |  |  |
| Air-Conditioner Failure |  |  |  |
| Tech Performing Test: | Phone/Pager: |
| Site CLLI: | Site Address: |
| Alarm Telemetry System Type: |
| X.25 overhead (fiber mux) | e-tel (Dantel, E2A, Westronics) | other (list) |
| NROC Tech with whom Test performed: | Phone: |
| Additional Notes: |

Form 846  Outside Plant Equipment Enclosure Housekeeping Alarm Verification

CONTENTS

Chapter and Section 	Page

16.	Definitions and Acronyms	16-1

# 16.	Definitions and Acronyms

| A or Amp | Amperes (amount of current flow) |
| --- | --- |
| A2LA | American Association for Laboratory Accreditation |
| ABC | Area Bus Centers |
| ABS | Alarm Battery Supply (small fusing at the power plant for the controller) |
| AC | 1) Alternating Current 2) Armor-Clad (certain cable types with a metallic wind outer jacket) |
| A/C | Air-Conditioning |
| ACEG | Alternating Current Equipment Ground |
| ach | air changes per hour |
| ACO | Alarm Cut-Off |
| ACT | Activate |
| AGM | Absorbed Glass Matte (VRLA battery separator-absorbed electrolyte) |
| AH or A-hr | Ampere-Hour (rating of a battery to deliver so many Amps for so many hrs) |
| A.I.C. | Amps of Interrupting Current (capability to withstand) |
| AID | Access IDentifier (identifies a specific piece of equipment) |
| aka | also known as |
| alm | Alarm |
| Alt | Alternator |
| ALW | Allow |
| ANCR | Abnormal Network Condition Report (Qwest outage reporting method) |
| ANSI | American National Standards Institute |
| ASCII | American Standard Characters for Information Interchange |
| ASHRAE | American Society of Heating, Refrigerating, and Air-conditioning Engineers |
| ASTM | American Society of Testing Materials |
| ATIS | Alliance for Telecommunications Industry Solutions |
| ATS | Automatic Transfer Switch/System |
| ATTR | Attribute |
| AWG | American Wire Gauge |
| BAT or Batt | Battery |

| BDB | Battery Distribution Board — see PBD |
| --- | --- |
| BDFB or BDCBB | Battery Distribution Fuse (or Circuit Breaker) Board/Bay |
| Bkr or Brkr | Breaker |
| BMS | Battery Management System |
| bps | bits per second |
| BVAPP | Billing Verification Authority Purchasing Project (Qwest job number) |
| BX | An older type of AC (armor-clad) cable |
| C | degrees Celsius, or battery Capacity, or Common (grounded) alarm contact |
| cab | cabinet |
| CANC | Cancel |
| cap | capacitor |
| CATV | traditional cable TV hybrid fiber-coax network |
| CB | Circuit Breaker |
| ccs | centi-call seconds (or hundreds of call seconds — full usage is 36 ccs/hr) |
| CdO | A small Central Office (Community Dial Office) |
| CEC™ | Controlled Environmental Cabinet (half-buried walk-in hut/vault) |
| CEM | Construction Engineering Memorandum |
| CEMF | Counter-Electro Motive Force cell |
| CEV | Controlled Environmental Vault |
| CFA | Converter Fail Alarm |
| CFR | Controlled Ferro-Resonant rectifier, or Code of Federal Regulations |
| Charger or Chg | Rectifier |
| ckt | circuit |
| CLEC | Collocated Local Exchange Carrier |
| CLLI™ | Common Language Location Identifier |
| Cntrl | Control |
| CO | Central Office |
| coax | coaxial waveguide cable |
| COE-FM | Central Office Equipment – Facilities Management |

| COGB | Central Office Ground Bus |
| --- | --- |
| COM or com | Communications, or commercial |
| COML | Commercial (AC) |
| COND | Condition |
| CONT | Control |
| conv | converter |
| CP | Chlorosulfonated Polyethylene (type of cable insulation) |
| Crit or CR | Critical alarm |
| CSPEC | Common Systems Planning and Engineering Center |
| CURNT or CUR | Current (in Amperes) |
| daisy chaining | running multiple bays/shelves off of a single fuse/breaker position |
| dBa | deciBels audible |
| dBrnC | deciBels referenced to noise weighting C (POTS voiceband) |
| DC | Direct Current |
| delta or Δ | method of providing 3-phase power |
| demarc | demarcation point between phone company and premises wiring |
| diff | differential |
| Disc | Disconnect |
| Dist | Distribution |
| DLC | Digital Loop Carrier |
| DLO | Diesel Locomotive (wire — Class K wire stranding) |
| DLT | Delete |
| DMS™ | Digital Multiplexing System (family of Nortel Class 5 switches) |
| drop | the smaller power wire, tapped to the main conductor, to enter a bay |
| DSCHRG | Discharge |
| DS-0 | Digital Signal (level) 0, a digital data rate of 64 kbp/s |
| DS-1 | Digital Signal 1, a digital data rate of 1.544 Mbps (can carry 24 DS-0s) |
| DS-3 | Digital Signal 3, a digital data rate of 50 Mbps (can carry 28 DS-1s) |
| DSL | Digital Subscriber Line (high speed copper carrying data or video) |
| DSU | Data Serving Unit (modem for packet circuits, like X.25) |

| DTMF | Dual Tone Multi-Frequency |
| --- | --- |
| EAT | Engine Alarm Termination box |
| ED | Edit |
| EDLC | Electric Double-Layer Capacitor (Super™ or Ultra™ Capacitor) |
| EEE | Electronic Equipment Enclosure |
| Emerg or Emg | Emergency |
| EMI | Electro-Magnetic Interference |
| EMT | Electrical Metallic Tubing |
| Eng | Engine |
| env | environment(al) |
| EPA | Environmental Protection Administration |
| EPO | Emergency Power Off switch |
| EPR/EPDM | Ethylene Propylene Rubber (a type of wire insulation material) |
| E/Q | Earthquake |
| eqpt | equipment |
| Equipment Bays | any equipment that is not the primary power source. |
| ESD | Electro-Static Discharge |
| ESS | Electronic Switching System |
| e-tel | e-telemetry (an alarm transport method over a 4-wire 9.6 kpbs circuit) |
| EXT | External |
| F | degrees Fahrenheit, or Farad (unit of capacitance) |
| FB | Fuse Bay |
| FCC | Federal Communications Commission |
| FR | Family of Requirements |
| FS | fuse |
| FX | Foreign Exchange |
| G | rectifier Group (number) |
| gal | gallon |
| GEN | Generator |
| genset | standby engine-alternator (typically the portable type) |

| GF(C)I | Ground Fault (Circuit) Interrupter |
| --- | --- |
| GND or GRD | Ground |
| GPDF | Global Power Distribution Frame for a Lucent 5ESS® switch |
| GPS | Galaxy™ Power System (from Lineage Power) |
| GR | Generic Requirements |
| Hardened Equipment | Equipment that must operate at the temperature extremes of -40° and +65° C. |
| HDR | Header |
| HI | High |
| hka | housekeeping (environmental or power) alarm |
| hp | horsepower |
| hr | hour |
| HSP | House Service Panel |
| html | Hyper-Text Markup Language |
| HVAC | Heating, Ventilation and Air-Conditioning |
| HVSD | High Voltage Shut Down |
| Hz | Hertz (frequency — cycles per second) |
| ICEP | Inductive Coordination and Electrical Protection |
| ICS | Industrial Controls and Systems |
| ID | IDentifier |
| IEC or IXC | InterExchange Carrier |
| IEEE | Institute of Electrical and Electronic Engineers |
| INH | Inhibit |
| INIT | Initialize |
| inv | inverter |
| IOF | Inter Office Facilities |
| IP | Internet Protocol |
| ISDN | Integrated Services Digital Network |
| k | kilo (1000) |
| K | constant representing the resistance of copper or aluminum |
| kcmil | kilo circular mils (a circular mil is the area of a circle with a dia. of 1/1000”) |

| KS | Kearney Specification (a manufacturing standard from Western Electric) |
| --- | --- |
| L- | List number (part of the end of some telecommunications part numbers) |
| LATA | Local Access Transport Area (separates local from long distance carrier call) |
| LED | Light Emitting Diode |
| LEL | Lower Explosive Limit |
| Li | Lithium |
| LMP | Lithium Metal Polymer (battery) |
| LNS | Local Network Services |
| LO | Low |
| LOI | Limiting Oxygen Index |
| LPDU | Load Power Distributing Unit for a 5ESS® switch |
| LPG | Liquid Propane Gas |
| LS | Low-Voltage Surge |
| LSSGR | LATA Switching System Generic Requirements |
| LVD | Low Voltage Disconnect |
| m | milli (thousandth) |
| M | mega (million), or thousand in the Roman numeral system |
| Maj or MJ | Major alarm |
| max | maximum |
| MC | Metal-Clad cable (a specialized type of armored cable that is sealed to gas) |
| MCM | thousand circular mils (old designation — modern one is kcmil) |
| MCS™ | Microprocessor Controlled System (Trademark of Lineage Power) |
| Mdl | Model (number) |
| MEAS | Measure |
| Mfg | Manufacturer |
| MG | Main Generation or Motor Generator |
| MGB | Main Ground Bus (in the Ground Window) |
| MI | Mineral Insulated cable (copper and magnesium-oxide outer jacket) |
| μ | micro (millionth, or precursor to processor) |
| m | milli (one thousandth) |

| min | minute, or minimum |
| --- | --- |
| Min or MN | Minor alarm |
| MOP | Method of Procedure (used to define installation steps) |
| MOV | Metal-Oxide Varistor |
| MSG | Message |
| mux | multiplexer |
| MVPC | minimum Volts per Cell |
| n | minimum number of rectifiers/converters/engines required to meet the load |
| N81 | No parity, 8 bits, 1 stop bit (modem communications protocol setting) |
| N.C. | Normally Closed contacts (open on alarm) |
| NE | intelligent Network Element |
| NEBS | Network Equipment – Building System |
| NEC | National Electrical Code |
| NEMA | National Electrical Manufacturer's Association |
| NFPA | National Fire Protection Association |
| Ni-Cad or NiCd | Nickel Cadmium |
| NID | Network Interface Device (demarc between company and premise wiring) |
| NMA™ | Network Monitoring and Analysis |
| NMH or NiMH | Nickel-Metal Hydride |
| NNS | National Network Services (of Qwest) |
| N.O. | Normally Open contacts (close on alarm) |
| NROC | Network Reliability and Operations Center (Qwest Alarm Center) |
| NRTL | Nationally Recognized Testing Laboratory |
| NTA | National Telecommunication Association |
| NVLAP | National Voluntary Laboratory Accreditation Program |
| OPGP(B) | Office Principal Ground Point (Bus) |
| OPR | Operate |
| ORM | Optical Remote (switching) Module |
| OSHA | Occupational Safety and Health Administration |
| OSP | Outside Plant |

| OSS | Operational Support Systems |
| --- | --- |
| PAD | Packet Assembler/Disassembler |
| PBD | Main DC Power Distribution Fuse/Breaker Board |
| PC | Pilot Cell |
| PDF | Power Distribution Frame |
| PDSC | Power Distribution Service Cabinet (AC cabinet feeding the rectifiers) |
| PDU | AC Power Distribution Unit (data center floor mount cabinet) |
| P.E. | Professional Engineer |
| PFC | Power Factor Correction |
| PF(D) | Power Fuse (Distribution) Bay for a switch |
| ph or Ø | Phase (of AC) |
| plt | plant |
| PNM | Public Service Company of New Mexico (an electric utility) |
| power factor or pf | the cosine of the phase angle between AC Voltage and current peaks |
| Power Room/Area | contains rectifiers, batteries, bus bars, controller, and PBDs |
| POTS | Plain Old Telephone Service |
| Prem | commercial Customer Premises |
| PROC | Processor |
| PSMC | Power System Monitor Controller |
| PSMC-CL | Power System Monitor Controller-Confined Locations |
| Pub | Publication |
| PV | photo-Voltaic |
| PVC | Poly-Vinyl Chloride (plastic) |
| Pwr | Power |
| Q&A | Question and Answer (Qwest Engineering tool) |
| R | Resistance or Restart |
| Rect | Rectifier |
| Reg | Regulation |
| REPT | Report |
| RFA | Rectifier Fail Alarm |

| RG | Regional (part of a standard practice or form number for Qwest LNS) |
| --- | --- |
| RHH | Rubber, extra-High temperature (wire insulation) |
| RHW | Rubber, High temperature, Water resistant (wire insulation) |
| RLS | Release |
| rms | Root Mean Square ("effective", "average" AC Voltage) |
| RNG | Ringing (plant) |
| ROH | Receiver Off Hook |
| RoHS | Reduction of Hazardous Substances |
| ROW | Right-of-Way |
| RPM or rpm | Remote Peripheral Monitor, or revolutions per minute |
| rptr | repeater |
| RR | Relay Rack |
| RS | Reverse Service, or Re-Start, or Recommended Standard |
| RT | Remote Terminal |
| RTN | Return (bus) |
| RTRV | Retrieve |
| RTU | Right-to-use |
| s or sec | second(s) |
| SAD | Silicon Avalanche Diode |
| SBR | Styrene Butadiene Rubber (cable insulation) |
| SECU | Secure |
| s.g. | Specific Gravity |
| SHNS | Self Healing Network Services (architecture sold by Qwest) |
| SHRPS | Self Healing Ring Protective Services (architecture sold by Qwest) |
| SID | System ID (the originating network element of a TL1 message or query) |
| SMR | Switch-Mode Rectifier |
| SNMP | Simple Network Management Protocol |
| SPCS | Stored Program Control Switching System |
| spec(s) | specification(s) |
| SR | Special Report |

| Stby | Standby |
| --- | --- |
| SW | Switch |
| Sys | System |
| T | Terminate or stop |
| T1 (or T-1) | T-carrier rate 1 — physical standard for carrying a DS-1 signal |
| TA | Technical Advisory |
| Tech or tech | Technical or technician |
| Temp | Temperature |
| term | termination or terminal (bar) |
| TFFN | Thermo-plastic, Flexible, Fixture wire, with Nylon jacket |
| TH | Threshold |
| THD | Total Harmonic Distortion (in the AC source or fed back to it) |
| THHN | Thermoplastic, extra-High temperature, Nylon-jacketed (wire insulation) |
| 3D Condo | A co-location building that is jointly owned. |
| THWN | Thermoplastic, High temperature, Water resistant, Nylon-jacketed insulation |
| TID | Target IDentifier (the network element to which a TL1 message is sent) |
| TIF | Telephone Influence Factor |
| TL1 | Transaction Language 1 (NE to NMA communication, defined by Telcordia) |
| TP | Test Point |
| TLS | Tape Library System |
| top to top | from the top of one equipment bay to another, not including drops |
| TPE | Thermo-Plastic Elastomer (wire insulation) |
| TR | Technical Reference, or Terminate Rectifier (shutdown signal) |
| Trbl | Trouble |
| TSGR | Transport System Generic Requirements |
| TVSS | Transit Voltage Surge Suppression |
| UBC | Uniform Building Code |
| UE™ | Universal Enclosure (half-buried walk-in hut/vault) |
| UFC | Uniform Fire Code |
| UL | Underwriter's Laboratory |

| UP | Upper |
| --- | --- |
| UPS | Uninterruptible Power Supply |
| USE | Underground Service Entrance (cable) |
| V | Volts |
| VA | Volt-Amps |
| VG | Voltage |
| VRLA | Valve Regulated Lead Acid |
| VT100 | Virtual Terminal Emulation with 100 defined keys |
| W | Watt (equal to Volt-Amps for DC, but reduced by the power factor for AC) |
| (Class) W | Welding wire stranding |
| WECO | Western Electric Company (manufacturing arm of the former Bell System) |
| wye or Y | three-phase power, where the center tap is grounded neutral |
| Xfr | Transfer |
| XHHW | Cross-linked, thermoset, extra-High temperature, Water resistant insulation |
| XLP | Cross-Linked Polyethylene (wire insulation) |

CONTENTS

Chapter and Section 	Page

17.	References	 17-1

17.1	Telcordia Publications	 17-1

17.2	Qwest Technical Publications	 17-2

17.3	Miscellaneous Publications	 17-2

17.4	Ordering Information	 17-5

# 17	References

All reference documents are latest available issues.

## 17.1	Telcordia Publications

BR-790-100-656	DC Distribution

GR-26-CORE	Generic Requirements for Controlled Environmental Vaults (CEVs)

GR-27-CORE	Generic Requirements for Environmental Control Systems for Electronic Equipment Enclosures

GR-63-CORE	Network Equipment-Building System (NEBS) Generic Equipment Requirements

GR-78-CORE	General Physical Design Requirements for Communications Products and Equipment

GR-230-CORE 	Generic Requirements for Engineering Complaints

GR-347-CORE	Generic Requirements for Central Office Power Wire

GR-811-CORE	TL1 Messages Index

GR-833-CORE	TL1 Surveillance and Maintenance Messages

GR-1089-CORE	Generic Requirements for Network Telecommunication Equipment.

TA-NWT-000370	Generic Requirements for Mechanized Power Room Operations Monitor (MPROM)

TR-TSY-000757	Generic Requirements for Uninterruptible Power Systems (UPS)

TR-NWT-000811	OTGR: Operations Application Messages - TL1 Message Index

TA-NWT-001360	Generic Requirements for Power Systems Messages at the OS/NE Interface

SR-3580	Network Equipment-Building System (NEBS) Criteria Levels

SR-4228	VRLA Battery String Certification Levels Based on Requirements for Safety and Performance

## 17.2	Qwest Technical Publications

PUB 77350	Central Office Telecommunications Equipment Engineering Installation and Removal Guidelines

PUB 77351	Qwest Communications, Inc. Engineering Standards

PUB 77354	Guidelines for Product Change Notices

PUB 77355	Grounding - Central Office and Remote Equipment Environment

PUB 77368	Commercial Customer Premises Electronic Equipment Environmental Specifications and Installation Guide

## 17.3	Miscellaneous Publications

ANSI C37.16	Low Voltage AC Power Circuit Breakers and AC Power Circuit Protectors – Preferred Ratings, Related Requirements, and Application Recommendations

ANSI C62.11	Metal-Oxide Surge Arrestors for Alternating Current Power Circuits

ANSI/IEEE C62.35	Standard Test Specifications for Avalanche Junction Semiconductor Surge Protective Devices

ANSI/IEEE C62.36	Standard Test Methods for Surge Protectors Used in Low-Voltage Data, Communications, and Signaling Circuits

ANSI/IEEE C62.41.1 Guide on the Surge Environment in Low-Voltage (1000V and Less) AC Power Circuits

ANSI/IEEE C62.41.2 Recommended Practice on Characterization of Surges in Low-Voltage (1000V and Less) AC Power Circuits

ANSI/IEEE C62.45	Recommended Practice on Surge Testing for Equipment Connected to Low-Voltage (1000V and Less) AC Power Circuits

ANSI/IEEE C62.62	Standard Test Specifications for Surge-Protective Devices for Low Voltage AC Power Circuits

ANSI C84.1	Electrical Power Systems and Equipment — Voltage Ratings (60 Hz)

ANSI T1.311	DC Power Systems — Telecommunications Environment Protection

ANSI T1.315	Voltage Levels for DC Powered Equipment Used in the Telecommunications Environment

ASTM B-8	Standard Specification for Concentric-Lay-Stranded Copper Conductor, Hard, Medium-Hard, or Soft

ASTM B-172	Standard Specification for Rope-Lay-Stranded Copper Conductor Having Bunch-Sheath Members, for Electrical Conductors

ASTM B-174	Standard Specification for Bunch-Stranded Copper Conductors for Electrical Conductors

ASTM D-975	Standard Specification for Diesel Fuel Oils

ATIS PP-0600003	Battery Enclosure and Rooms/Areas

IEEE 115	Test Procedures for Synchronous Machines

IEEE 484	Recommended Practice for the Design and Installation of Vented Lead-Acid Batteries for Stationary Applications

IEEE 485	Recommended Practice for Sizing Lead-Acid Batteries for Stationary Applications

IEEE 1187	Recommended Practice for the Design and Installation of Valve-Regulated Lead-Acid Storage Batteries for Stationary Applications

IEEE 1189	Guide for the Selection of Valve-Regulated Lead-Acid Batteries for Stationary Applications

IEEE 1375	Guide for the Protection of Large Stationary Battery Systems

IEEE/ASHRAE1635	Guide for the Ventilation and Thermal Management of Stationary Battery Installations

IEEE C62.22	Guide for Application of Metal-Oxide Surge Arresters for Alternating-Current Systems

IEEE C62.34	Standard for Performance of Low-Voltage Surge-Protective Devices (Secondary Arresters)

IEEE C62.35	Standard Test Specifications for Avalanche Junction Semiconductor Surge Protective Devices

IEEE C62.41	Recommended Practice for Surge Voltages in Low-Voltage AC Power Circuits

IEEE C62.64	Standard Specifications for Surge Protectors Used in Low-Voltage Data, Communications and Signaling Circuits

IFC	International Fire Code, published by the International Code Council

NEMA ICS 10	Part 1:  Electromechanical AC Transfer Switch Equipment

NEMA LS 1	Low Voltage Surge Suppression Devices

NEMA MG 1	Motors and Generators

NFPA 1	Uniform Fire Code

NFPA 30	Flammable and Combustible Liquid Code

NFPA 37	Standard for the Installation and Use of Stationary Combustion Engines and Gas Turbines

NFPA 70	National Electrical Code

NFPA 101	Life Safety Code

NFPA 110	Standard for Emergency and Standby Power Systems

OSHA 29CFR	Part 1910, Department of Labor, Occupational Safety and Health Standards

UBC	the Uniform Building Code, published by the International Conference of Building Officials (ICBO)

UFC	Uniform Fire Code, published by the Western Fire Chiefs Association (WFCA)

UL 94	Test for Flammability of Plastic Materials for Parts in Devices and Applications

UL 1008	Standard for Transfer Switch Equipment

UL 1066	Standard for Low Voltage AC and DC Power Circuit Breakers Used in Enclosures

UL 1449	Transient Voltage Surge Suppressors

UL 1950/60950	Safety of Information Technology Equipment, Including Electrical Business Equipment

## 17.4	Ordering Information

All documents are subject to change and their citation in this document reflects the most current information available at the time of printing.  Readers are advised to check status and availability of all documents.

Obtain:

American National Standards Institute (ANSI) documents from:

American National Standards Institute 
Attn: Customer Service
11 West 42nd Street
New York, NY 10036
Phone:  (212) 642-4900
Fax:  (212) 302-1286

www.ansi.org

American Society for the Testing of Materials (ASTM) documents from:

American Society for the Testing of Materials 
100 Bar Harbor Dr.

P.O. Box C700
West Conshohocken, PA 19428
Phone:  (610) 832-9585
Fax:  (610) 832-9555

www.astm.com

Alliance for Telecommunications Industry Solutions (ATIS) documents from:

Alliance for Telecommunications Industry Solutions 
1200 G St. NW

Washington, DC 20005
Phone:  (202) 628-6380
Fax:  (202) 393-5453

www.atis.org

IEEE documents from:

IEEE Customer Service Center

445 Hoes Lane

Piscataway NJ, 08855-1331

Phone:  (800) 678-4333

Fax:  (732) 981-9667

www.ieee.org

International Building and Fire Code documents from:

International Code Council

5203 Leesburg Pike, Ste. 600

Falls Church, VA 22041

Phone:  (703) 931-4533

www.iccsafe.org

NEMA documents from:

National Electrical Manufacturers Association

www.nema.org

NFPA documents from:

NFPA Customer Sales

1 Batterymarch Park

Quincy, MA 02269-9101

Phone:  (800) 344-3555

Fax:  (617) 770-0700

www.nfpa.org

Qwest Technical Publications from:

www.qwest.com/techpub

Telcordia documents from:

Telcordia - Customer Services 
8 Corporate Place
Piscataway, NJ 08854-4196
Telex:  (201) 275-2090
Fax:  (908) 336-2559
Phone:  (800) 521-2673

www.telcordia.com

UL documents from:

Underwriters Laboratories

Phone:  (888) 853-3503

www.ul.com

# Text boxes

All fuse positions must be installed from the bottom up to avoid cable congestion and for the safety of the installer adding future fuses.